Project Gutenberg's Central-Station Electric Lighting, by Killingworth Hedges

This eBook is for the use of anyone anywhere in the United States and

most other parts of the world at no cost and with almost no restrictions

whatsoever.  You may copy it, give it away or re-use it under the terms

of the Project Gutenberg License included with this eBook or online at

www.gutenberg.org.  If you are not located in the United States, you'll

have to check the laws of the country where you are located before using

this ebook.

Title: Central-Station Electric Lighting

With Notes on the Methods Used for the Distribution of Electricity

Author: Killingworth Hedges

Release Date: January 22, 2020 [EBook #61219]

Language: English

Character set encoding: UTF-8

*** START OF THIS PROJECT GUTENBERG EBOOK CENTRAL-STATION ELECTRIC LIGHTING ***

Produced by Chris Curnow, Paul Marshall and the Online

Distributed Proofreading Team at http://www.pgdp.net (This

file was produced from images generously made available

by The Internet Archive)

Transcriber’s Notes:

Underscores “_” before and after a word or phrase indicate _italics_

in the original text.

Equal signs “=” before and after a word or phrase indicate =bold=

in the original text.

Small capitals have been converted to SOLID capitals.

Illustrations have been moved so they do not break up paragraphs.

Typographical errors have been silently corrected.

The three advertisements at the beginning of the book have been

moved in front of the thirteen advertisements at the back of the

book.

CENTRAL-STATION

ELECTRIC LIGHTING

WITH

NOTES ON THE METHODS USED FOR THE

DISTRIBUTION OF ELECTRICITY.

BY

KILLINGWORTH HEDGES,

MEMBER OF THE INSTITUTION OF CIVIL ENGINEERS, AND OF THE

SOCIETY OF TELEGRAPH ENGINEERS AND ELECTRICIANS.

[Illustration]

LONDON:

E. & F. N. SPON, 125, STRAND.

NEW YORK: 12, CORTLANDT STREET.

[_All rights reserved._]

PREFACE.

The art of lighting by Electricity practically dates from ten years

ago, and it has during that period received the constant attention of

both Electrical Engineers and others, who have applied the greatest

scientific knowledge. The result of all this energy appears to be

discouraging. Five hundred thousand pounds have been subscribed to

carry on the business, and it is doubtful whether the companies which

survive have a market value of one-tenth of that sum. The experience

may have been bought too dearly, but the era of Central-Station

Electric Lighting, which has now commenced, ought to re-establish the

position of Electricity in financial circles, and afford a safe and

profitable outlet for the surplus capital of the investor who buys gas

and water shares to pay four per cent.

The distribution of electricity from a central-station, which was the

subject of Sir William Siemen’s Presidential Address at the Society of

Arts in 1882, is not only accomplished from the scientific point of

view, but is also a commercial success: the power of flowing water, or

the potential energy stored up in coal, wood, or other fuel, can be

utilised for lighting our streets and houses at night, and during the

day may be transmitted by means of electricity in the easiest possible

way, and supplant the gas-engine for driving small machinery.

A paper entitled “Central-Station Electric Lighting” was contributed by

the Author to the Institution of Civil Engineers, and was published in

Part II. of the Minutes, 1886-87; the subject-matter has been extended

and brought up to date, with the object of giving a description of the

systems which are practically employed in Central-Station Lighting at

home and on the Continent. Details respecting the generating plant at

these stations are omitted on purpose; technical terms would also be

avoided if possible; failing this, it is hoped that the accompanying

Glossary will explain what is unfamiliar.

The amendment of the Electric Lighting Act of 1882 has given a fresh

stimulus to the industry, and many new enterprises for distributing

electricity from Central-Stations are being prepared, and it is to

be hoped that the public will profit by former experience, and will

discriminate between the good and the bad schemes which will be offered

to them.

The organizing facilities possessed by Gas Companies make it desirable

that they should follow the example of the American Companies, and

take up the business of supplying electricity. The existing powers of

private companies might have to be altered, but those municipal

authorities who own the gasworks could certainly distribute electricity

from a central-station, which might be installed at the present works.

Local authorities have certain advantages over private companies

owing to the purchasing clause of the Electric Lighting Act, also the

power to borrow money under this and the Local Loans Act of 1875;

should there be no department to carry out the business of supplying

electricity, the generating plant could be maintained and worked by a

contractor for a fixed annual sum.

The remarks of Lord Herschell that the “electric light is more used in

the South Sea Islands than in this country” ought to be taken as not

so much referring to want of enterprise on the part of capitalists and

engineers, but to the Electrical Facilities Act of 1882, which has been

appropriately termed a very “boa-constrictor.”

KILLINGWORTH HEDGES.

25, QUEEN ANNE’S GATE,

WESTMINSTER, S.W.

_September, 1888._

INDEX OF TERMS.

AMPÈRE-HOUR.—A current of one ampère strength

for one hour.

CURRENT, CONTINUOUS.—The flow of electricity

in one direction.

CURRENT, ALTERNATING.—The intermittent flow

in two directions.

CONDUCTOR.—The wire through which the current

passes.

CIRCUIT, PRIMARY.—With transformers, the

conductor or leads attached to the dynamo.

CIRCUIT, SECONDARY.—With transformers, the

conductor from the transformer to the lamps.

C. P.—Abbreviation of Candle-power.

E. M. F.—Abbreviation of Electro-motive force.

LIFE OF INCANDESCENT LAMPS.—The duration of

the filament which produces the light.

POTENTIAL.—Difference of E. M. F., or High

and Low-Tension.

_See also Glossary, or Explanation of Terms_, page 107.

AN ELECTRICAL CENTRAL-STATION.

As the term “central-station” associates itself with some pretentious

building, such as a railway terminus, it may be advisable to remark

that the similarity is only in the words, and that central-station is

an abbreviation of central generating station, or building designed to

contain the plant for the public supply of electricity. In the early

days of electric lighting the transmission of electricity to a distance

was considered an impossibility; we find the late Sir William Siemens,

in his Presidential Address at the Society of Arts on the occasion of

the opening of the session in 1882, stating “that a quarter of a mile

in every direction from the lighting station was the area which would

be as much as could be economically worked;” and, in order to tap the

most paying district, it was proposed to establish a station in the

most central spot. Sir William Siemens suggested the utilisation of

the public squares, which could be excavated to a depth of twenty-five

feet, and then arched over to the existing ground level, and in this

covered space the engines, boilers, and dynamos were to be fixed;

the only erection above the surface was the chimney, which was to be

of ornamental design and combined with the ventilating arrangements

of the subterranean chamber. The great inventor, who so ably filled

the presidential chair at the meeting where these words were spoken,

would be astonished to find that in London one electric lighting

company has already erected seventy miles of overhead wire, and that

customers are supplied miles away from the so-called central-station.

The changed position of electricity is due to the introduction of the

transformer by Goulard, who showed, at the Turin Exhibition of 1884,

that a high-tension current could be transformed into a low-tension

working current of safe potential, fifty miles away from the generator,

in a successful and economical manner, and that the generating station

might, therefore, be located outside the area to be lighted. In large

cities this is a great advantage, the value of land often precluding

the erection of a big station in the working area; for this reason

small stations are often arranged in basements, under a large building,

which are, as a rule, specially designed. This plan is somewhat similar

to that adopted in the United States, where it is not unusual to

find a successful installation in a basement and sub-basement, the

general arrangement being of similar character to the engine-room of a

steamship.

A station is being erected in Philadelphia on a ground space of 72

feet × 100 feet, which is to supply 60,000 lights; the building is

six-storied, the dynamos are on the first floor, the boilers on third,

the coal stores on fourth, and the offices on the fifth.

The term “block station” is also used in the United States and in

Germany, and is applied to an installation which lights a group of

buildings or block without crossing any streets, and consequently

without having any wayleave or permission from local authorities.

CENTRAL-STATION CONSTRUCTION.

An American electrical engineer graphically sums up this question

in the following manner:—“There are two ways of starting a

central-station for electric lighting—the investment or the

speculative plan, or the fair means or the foul. The first has

its legitimate end, but the latter is the border ruffian or

money-or-your-life policy, which enters a territory already

sufficiently covered, not for fair competition, but to make money by

being bought out.” Happily, here, we have at present only to deal

with the first plan, and the question naturally arises, “Is electric

lighting a paying investment?” It certainly will not be if the object in

view is only to compete with gas in a limited district where perhaps

it is being sold at 2_s._ 6_d._ per 1000 feet, for, as long as there

is a ready market for the coke and other by-products, gas will remain

in possession of the field. The heat from gas, which is found so

undesirable by the wealthier classes, is advantageous to those who

perhaps cannot afford a fire; in fact, gas has been truly called

the “poor man’s friend,” and, until electricity can be supplied at

a nominal price, it will be useless to expect any revenue from the

poorer districts of large cities. Quite an opposite result may be

looked for when the electric mains are laid at the doors of the wealthy

householder, or through the business neighbourhoods. Shop-owners

especially are found to immediately take up electric light, from the

fact that no fumes are given off to destroy goods or tarnish silver

or gilding, and because it can be so easily applied in a shop window

so as to efficiently light the contents without producing shadows.

The great object to be aimed at in selecting a district to be served

from a central-station is a “constant demand,” and for this reason

it is advantageous to include a business neighbourhood with shops,

public-houses, and restaurants, which require the light for a definite

period every day, and probably will each take more than double the

amount of an ordinary dwelling-house; in fashionable neighbourhoods

especially, it is not unusual to find a large number of houses vacated

at the close of the season, the interest on that portion of the

electric system which is unemployed will have to be set against the

profits of other periods of the year.

The number of gas lights which are actually used at one time in a house

is found to average only two-thirds of the total number fixed, and

with electric light this number is reduced to one-half; economy is at

once the rule with electric light, partly because of the novelty of

the illuminant, and also on account of the facility of lighting and

extinguishing by simply turning a tap or switch. The number of hours

artificial light is wanted in a residential district may be taken at

about 1000 hours per annum, that is to say, the light is required for

about four hours a day in winter and two hours in summer; this amount

is very much exceeded in clubs, shops, and even in large houses, but

1000 hours is a safe figure, and, if the supply is taken by meter,

an annual payment equivalent to 1000 hours’ supply should be a fixed

amount to be paid for, whether used or not. Mr. Crompton estimates

that a Londoner, who is a tenant or owner of a house having three

reception rooms, ten bedrooms, and usual offices, spends about £25 a

year for his lighting, which is made up as follows:—gas bill, £15;

lamp, oil, candles, matches, about £10. There would be about fifty

burners fixed; and, supposing fifty electric lights to be substituted,

he could be supplied with electricity for £25 a year, at a fair profit

to the supply company if they charged 8_d._ per Board of Trade Unit,

as practice has shown that the total number of lamp-hours with fifty

electric lamps is not more than sixty-two, so that two Units,[1] or

1_s._ 4_d._ per day, would be sufficient for the lights he would

require.

[1] Unit; see page 7.

The diagram, Fig. 1, taken from a London residential district, shows

how the number of lamps on at one time vary; the district is supposed

to be wired for 10,000 lamps, and the plant as equal to the supply of

600 kilowatts, or 600,000 watts; the number of lamps is small until

about 3 o’clock, when it gets dusk on a winter afternoon; it then

increases steadily until about 6.30 o’clock, when the curve goes up

with a rush; about this time a great number of people are preparing for

dinner, and probably the lights are on both in the dining-room and

bedrooms. The curve falls, and at about 8 it begins to sink gradually

until 10 o’clock; a great many people appear to go to bed about this

time, but a few sit up to 1 o’clock; until 6 the next morning hardly

any supply is taken, when the servants get up and prepare the rooms

for the day. The diagram, Fig. 2, is taken from the Edison Company’s

central-station at Cincinnati, and agrees fairly with the London

demand for light. Another interesting fact has been ascertained from

the observations taken at the Mauer Strasse station in Berlin, namely,

that the output varies with the temperature, it goes up or down with

the thermometer. The reason is easily explained; gas is laid on side

by side with the incandescent lamps, and the burners are first lighted

when it is cold to warm the apartments; in warm weather the electric

light alone is used. From these and other diagrams the very important

fact has been obtained, that the average daily output of a station

throughout the year is less than one-third of the total capacity of

the generating machinery, so that, although the station from which

the diagram in Fig. 1 was taken could maintain 10,000 16 candle-power

lamps simultaneously alight, the average daily output of electricity

would only equal 3500 constantly lighted; and, as the first cost of the

station is dependent on the size of the plant, the saleable output is

the important factor which governs the profits.

[Illustration: FIG. 1.]

[Illustration: FIG. 2.]

CHARGES FOR ELECTRICITY.

The well-known expression “per 1000 Cubic Feet” is not applicable to

electric light, and, instead, the Board of Trade Unit is employed.

By this term Unit is meant the quantity of energy contained in a

current of 1000 Ampères flowing under an Electro-motive Force of One

Volt during One Hour. In the early days of electric lighting the term

Volt-ampère was used, and has for convenience sake been shortened to

Watt; that is, the Volt or Unit of Electro-motive Force (or pressure)

is multiplied by the Ampère or Unit of current.

The Board of Trade Unit is, therefore, a Thousand Volt-ampères or Watts

per hour.

For example: 16 candle-power Swan lamps are assumed to take 60

Watts, which, if the electrical pressure is 100 Volts, would mean a

consumption of 0·6 Ampère; and, as an Electrical Horse-power equals 746

Watts, 12·4 lamps should theoretically be obtained per Horse-power,

which is, however, reduced in actual practice to 10 at the most, often

less.

The charge per Unit supplied by meter varies in England from 1_s._ to

7_d._

Price for electric            Equivalent price for gas of equal

light.                               light.

_s._  _d._                _s._   _d._

1     0     } per Board { 6     10      per 1000 cubic feet.

0     9     }     of    { 5      1½      ”         ”

0     7¼    }   Trade   { 4      2       ”         ”

0     6     }   Unit.   { 3      5       ”         ”

_Comparison of Cost of Gas and Electricity._

These prices, of course, include the manufacturer’s profit as well as

the loss in transmission through the mains and expenses of connecting

up to the consumer. The actual manufacturing cost of a station

maintaining 10,000 lights should not be more than 3_d._ per Unit, or

equivalent to gas at 1_s._ 8½_d._ per 1000 cubic feet.[2]

[2] See Table IV., page 87.

As petroleum lamps are used for the street lighting of many foreign

and colonial towns, the question arises, “Will it pay to substitute the

electric light?” Comparing the light given by a kerosene or petroleum

lamp with that from the incandescent electric lamp, the cost is greatly

in favour of oil; and, in fact, where the price of kerosene is under

1_s._ per gallon, electricity cannot compete if labour is cheap. On the

other hand, the trimming, lighting, and keeping in order of a number of

lamps scattered over a large area greatly augments the working cost, to

which must be added the breakages of chimneys, expense of wicks, also

the danger of fire. It is the safety of electricity which has caused

it to supplant oil both for public and private lighting in American

cities; even where the price of kerosene is not more than 6_d._ per

gallon there is a demand for the electric light, which is by far the

dearer illuminant, after making a liberal allowance for labour in

cleaning, filling, and lighting the oil lamp, also for depreciation of

the burners.

_Arc and Incandescent or Glow Lighting._

[Illustration: FIG. 3.]

Electric lighting can be obtained by means of arc or incandescent

lamps. The arc light is now well understood to be caused by the

extremely high temperature of the end of one or both the carbon

electrodes. The voltaic arc, Fig. 3, is formed by the minute particles

of carbon in a high state of combustion which the current appears

to break off and carry from one electrode to the other, the light,

however, being mainly due to the incandescence of the crater shown in

Fig. 3 on the upper carbon. In the incandescent or glow lamp light

is produced by the passage of a current of electricity through a

continuous fine thread or filament of carbon which becomes white-hot,

the destruction of the filament being prevented through its enclosure

in a glass bulb from which the air is exhausted. Figs. 4 and 5.

The first method is suitable for the lighting of streets where a

high-class illumination is required; also will be wanted for the

external lighting of shops, public-houses, and places of amusement, so

that arrangements must be made for arc lighting. The usual plan is to

charge at the same rate per Unit by meter as the incandescent lamps,

but to make an additional charge of 5_s._ to 7_s._ 6_d._ per lamp per

quarter for rent, and a further charge of 3_s._ per week for cleaning

and trimming.

The principal types are the Edison and the Swan, Fig. 4 and Fig. 5.

Incandescent lamps can be obtained to order from 1½ candle-power

upwards, but the 16 candle-power (nominal 20) or the 8 candle-power

(nominal 10) lamps are almost invariably employed. The latter give the

best effect, and can be worked to 10 candle-power without much risk,

they take about 30 watts as against 60 watts for the 16 candles; and

are not uneconomical, for nearly double the number can be worked with

the same energy. A new type of glow lamp, called the “Sunbeam,” has

been recently introduced, which contains a thick filament, and gives a

light of from 200 to 1500 candle-power, and can be employed instead of

an arc lamp with the same economy as the ordinary 16 candle-power type.

[Illustration: FIG. 4. FIG. 5.]

_Life of Incandescent Lamps._

In estimating the annual cost of lighting, the renewals of lamps must

be taken into account; and although some lamps have worked 3000 or even

4000 hours, a life of 1000 working hours is the highest average it is

safe to assume in practical work under even the best conditions, that

is, using secondary batteries and never over running. The average

life of 130 lamps on H.M.S. troopship _Malabar_ was 3799 hours each,

the shortest life being 638½ hours for 18 yard-arm lamps of 32

candle-power. If the current is allowed to fluctuate, the average life

would be very much less; it is an unsettled question whether long-lived

lamps are really economical, by reason of the blackening of the globes,

which takes place after the lamp has been worked some time, and is

probably due to small particles of carbon thrown off from the filament

being deposited on the glass. It has been suggested that attrition of

the filament is going on all the time the lamp is at work, and that

the heated atoms striking against the filament may account for the

blackening, in that the mean free path of the atoms would be greater

in a perfect vacuum than in the air, consequently they would abrade

the filament with considerable force. If lamps were sold at 1_s._ each

instead of 3_s._ 6_d._, which is now the price for not less than a

thousand, it would be more economical to change them at the first signs

of blackening, even if the life did not exceed 500 hours.

The diagram, Fig. 6, has been so arranged that the amount of light

required in a given district can be ascertained for any period of the

day or night; it has been calculated from the observations taken daily

at one of the Berlin central-stations by the engineer to the company.

Six hundred and forty watts are assumed, for the purposes of the

diagram, to be the equivalent of a horse-power, instead of 736, as the

German electrical horse-power is 736 watts instead of 746 watts.

[Illustration: FIG. 6.]

The table, Fig. 6, has two vertical scales, A and B, each giving the

kilowatts[3] and corresponding horse-power. A is drawn to a scale ten

times greater than B, with the object of noting the smaller amount of

lights required for street illumination. The horizontal line is divided

into hours, and represents a day’s lighting in the middle of December

and the end of July, so as to show the maximum and minimum amount of

current that will be required. In the lighting of a town there are

two classes of illumination, the amount taken by the public, which is

uncertain, and that employed for street lighting, which is a known

quantity.

[3] 1000 watts.

The curves, II and II A, represent the private lighting of houses,

hotels, theatres, and shops of different kinds in December and in

July, the curve, II A, being in dotted lines clearly shows what a vast

difference there is in the amount of light, and consequently the amount

of energy required in the generating station, as compared with curve

II, which is taken when the days are longest.

The rectangles, I and I A, show the street illumination, and are drawn

to suit scale A; half an hour after sunset all the lamps are turned on,

and the work reaches its maximum suddenly, and continues the same until

12 o’clock, when, according to the municipal decrees, it either falls

one or two gradations until half an hour before sunrise, when all the

lamps are extinguished. The calculations are based on the assumption of

640 watts to the horse-power, instead of 736, which is the theoretical

efficiency of a German horse-power.

If a number of diagrams are taken on this method for different periods

of the year, the constant work can be ascertained. This knowledge is

most valuable when calculating the most economical area for the mains,

which is then easily accomplished by means of Forbes’ tables, which are

based on Sir William Thomson’s well-known rule.

The lines, 2 and 2 A show the constant work at the same two

periods of the year from which the diagrams are taken. The constant

work at the end of December will be found to amount to 20 per cent.

of the total work, and that at the middle of June to 15 per cent. By

summing up the average work for all the days in the year we obtain the

cost per annum, and adding to this the expense of management, interest,

&c., and knowing the local conditions, we can fix what proportion of

the day’s work is admissible as loss. With the Edison system at Berlin,

5 per cent. is taken as average loss; thus, at the end of December,

it amounts, with the maximum number of lights, to 18·8 per cent., and

with the minimum to 1·1 per cent.; in the middle of July the maximum

is 15·8 per cent., and the minimum 0·5 per cent. The dynamos must, of

course, be of sufficient power to be able to overcome this loss, which

only shows itself periodically; therefore the generating plant may

be constructed to give, nominally, 20 to 30 per cent. less than the

maximum work, and be capable of being pushed to the full amount for a

short time only.

THE POSITION OF CENTRAL-STATION LIGHTING.

Uncontrolled financial speculation, aided by the stringent clauses of

the Electric Lighting Act of 1882, have been a great deterrent to the

extension of old or the introduction of new schemes for the supply of

electricity to the public in the same manner as gas. The President of

the Board of Trade, replying to a question in the House of Commons,

said that, “since the passing of the Electric Lighting Act of 1882,

fifty-nine provisional orders and five licences had been granted to

companies, and fifteen provisional orders and two licences to local

authorities. He was not aware that, in any single case where these

powers had been obtained, they had been exercised.” Up to the present

time no company supplying electricity has been under the necessity of

applying for compulsory powers, and has either obtained permission

from the local authorities to take up the streets, or has carried the

electric mains over the houses, and, regardless of the question of

overhead wires, has depended on wayleaves granted by the too-confiding

householder, who has no idea that his roof is supporting a cable

weighing 1¾ tons to the mile.

An amendment of the Act of 1882 has passed both Houses without

hindrance, and has received the Royal assent. It provides that in the

case of Provisional Orders the period after which the undertaking may

be bought up by the Local Authority shall be extended from twenty-one

to forty-two years, and that portion of the previous Act which referred

to the compulsory purchase of the undertaking by a local authority at

the end of the term has been altered, and more favourable terms given

to the electric companies.

On the Continent, and in the United States, where each city may be said

to legislate for itself in matters relating to the general welfare of

its citizens, the electric lighting industry is in a very different

position, and central-stations are either established or about to

be started in every important town. There were, in 1887, 121 Edison

central-stations alone, supplying over 323,000 incandescent lamps, and

paying dividends from 6 to 14 per cent. The Westinghouse Company, who

use a transformer system which is a modification of the Goulard and

Gibbs, have a hundred stations, maintaining 191,000 lamps, although

the first Westinghouse plant was put down only three years ago. The

progress in the United States is so rapid, and there are so many

successful applications of central-station lighting, that the subject

becomes too large to be even summarised, so that it is proposed to

treat in the following pages with some of the principal installations

on the Continent and at home.

Travellers abroad are accustomed to find electric lighting installed in

the most out-of-the-way places, especially in Switzerland, where water

power is abundant and is utilised to generate electricity, so that in

small hamlets arc lighting is often employed, and the visitors to the

local hotel will find it lit throughout by electricity. Electric light

stations in England are, with one exception, small in comparison with

those on the Continent. The most important is that at the Grosvenor

Gallery, London, which has increased from small beginnings until

it now supplies 20,000 glow lamps on sixteen circuits, the total

length of which is seventy miles. The next largest, which have been

in practical work for some time, are the Brighton and Eastbourne

stations, from which small installations of glow and arc lights are

maintained in various districts of the two towns. That the question

of cost or trouble, and the annoyance of machinery when erected in a

dwelling-house, do not altogether prevent the adoption of a superior

light, is clearly proved by the increasing number of householders, who,

after waiting in vain for electricity to be brought to their doors,

have set up the plant necessary to produce it themselves, and find no

practical difficulty in doing so. There are also many important public

works where electric light has been exclusively adopted. For instance,

at the Tilbury Docks there are 1350 glow and 80 arc lamps, distributed

over an area of 300 acres, and including the lighting of an hotel, dock

sheds, warehouse, signal-boxes, and offices. The London, Chatham, and

Dover station at Victoria has also been electrically lighted for the

past three years, the current being obtained from a central-station,

which was erected for the purpose of supplying electricity to the

Victoria district, and for which a provisional order was obtained.

This, however, has since been abandoned, although £16,000 had been

expended on plant and buildings by the promoters, who preferred to

postpone the scheme rather than to submit to the onerous 27th clause of

the Electric Lighting Act. Another still larger installation has been

put down to supply electricity to the Paddington station and district

of the Great Western Railway, as far as Westbourne Park. It embraces

an area of sixty-seven acres, and is lighted by 4115 glow and 98 arc

lamps. The system adopted is that designed by Mr. J. E. Gordon, and has

now been successfully worked for some time; but the many accessories

which are introduced, such as telephones, telegraphs, and indicators,

make it complicated in comparison with gas, or even with the ordinary

electric light systems. The current is generated by two dynamos, each

weighing 45 tons, and having revolving magnet wheels 9 feet 8 inches

in diameter, 22 tons in weight, a third machine being kept in reserve.

These dynamos are separately excited, and produce alternating currents.

The electricity is led to a large switch-board for distribution

throughout the district by means of five sub-stations; and from this

board there branches a double system of mains, which run everywhere

side by side, one-half the mains being connected to the first machine

and one-half to the second, so forming an excellent arrangement for

the prevention of total extinction of the light. The mains running to

the sub-stations are on the divided system, which is introduced for

the purpose of saving copper, as in a solid cable the loss of pressure

is greatest when the full number of lamps is on, and decreases as the

lamps are extinguished. With the divided main system it is intended to

follow out Sir William Thomson’s formula, which equates the value of

the loss of head, and the interest on the saving on the copper. If for

a certain main this formula shows that a fall of 20 per cent. is the

most economical condition for working, then, since by the divided main

the pressure can be kept within a variation of 2 per cent. at the

distant end, it follows that a considerable saving can be effected over

an ordinary solid main. Special arrangements are adopted at Paddington

to keep the pressure constant, a fall of potential being allowed for;

thus at the engine-house the pressure is 150 volts, in the passenger

station it is 120 volts, and at Westbourne Park it is 100 volts. The

arc lamps are fed by the same mains, and are arranged two in series.

A small installation at Kensington Court, erected two years ago, for

the purpose of supplying the houses in the immediate neighbourhood,

has rapidly developed, and underground mains have been led in many

directions from the station, and a constant service of electricity

is provided for by means of secondary batteries. As this is the

first practical exposition of the secondary batteries’ system of

distribution, it is proposed to describe the installation under that

head. Central-stations are also at work in Liverpool, Leamington,

Taunton, Exeter, and there are also five large installations nearly

completed in London, besides the Kensington Court station, all of which

will probably be in full swing before the end of the year.

ELECTRIC LIGHTING from CENTRAL-STATIONS is now practically carried out

on five different methods.

I. BY SECONDARY GENERATORS OR TRANSFORMERS, WITH ALTERNATING

CURRENT.

II. THE EDISON OR PARALLEL SYSTEM, WITH CONTINUOUS CURRENT.

III. THE SERIES OR BERNSTEIN SYSTEM.

IV. MULTIPLE SERIES.

V. DISTRIBUTION WITH SECONDARY BATTERIES OR ACCUMULATORS.

CLASS I.

SUPPLY BY SECONDARY GENERATORS OR TRANSFORMERS.

The problem of electric lighting from central-stations is comparatively

easy if an area can be obtained immediately surrounding, and within a

short distance of, the station, with a right of way for laying down the

electric mains direct. This happy state of affairs has not yet been

attained, consequently the generating station has more often to be in

an out-of-the-way corner of the district to be lighted, and it would be

financially impossible to use low-tension currents with correspondingly

large mains. The difficulty has been overcome in several ways by the

use of high-tension currents in the mains, and has led to the adoption

of secondary generators or transformers of electricity, which by

induction supply a current of low potential in the house-service. The

first to make this plan a practical success was Mr. Goulard, to whom

the honour of the introduction is due, although his claims as the first

inventor have been recently upset by the decision of the Courts.

The relative economy of the supply of electricity by the use of a

transformer is clearly shown by the following diagram, Fig. 7. A, B,

and C give proportionately the area of cross section of the total mass

of copper necessary to supply 5000 16 candle-power glow lamps situated

at a mean distance of 4000 feet from the dynamo. A refers to the

Edison “three-wire” system, working at a potential or electrical

pressure of 200 volts with a fall of potential or loss of energy in the

distributing feeders of 10 per cent., average distance from dynamo 4000

feet—the usual conditions on which this system is worked. B shows the

size of conductor required for the same work in an installation based

on the transformer system, potential 1000 volts, allowing 2·5 per cent.

loss in the supply mains—only one-fourth as much as in the direct

Edison system at the same average distance from dynamo. If this loss

were increased to 10 per cent., and made equal to that in the direct

system, viz. 10 per cent., the size of the conductor would be that

shown at C.

[Illustration: FIG. 7.]

[Illustration: FIG. 8.]

The graphic diagram, Fig. 8, demonstrates what the relative cost would

be with each of the three conditions just named.

Mr. Goulard’s first practical application of the secondary generator

in this country was the lighting of the Underground Railway Stations,

in 1883, from Edgware Road to High Street, the generating dynamo being

fixed at the former place. These experiments, which were made by Mr.

Kenneth Mackenzie, attracted considerable attention at the time, but

it was not until the report of the jurors to the Turin International

Exhibition in 1885 was published that companies were formed to instal

the Goulard system for lighting an extensive district.

[Illustration: FIG. 9.]

The principle underlying all transformers is that of the induction

coil invented by Ruhmkorff in 1842, but described by Faraday in his

“Experimental Researches,” published in 1831-2.

Fig. 9 is a diagram of the ordinary induction coil; on a central core

is wound a short length of thick wire called the primary, and again

over this is wound a greater length of fine insulated copper wire which

forms the secondary coil. On sending a low-pressure current from the

generator round the thick wire, a much smaller high-tension current is

induced in the secondary. A contact breaker is employed to make and

break the current, or, as in the early instruments, a commutator may be

used to produce the alternations. When used as a transformer the action

is reversed, that is, a high-tension current is passed through the

primary coil, which is composed of a wire of small sectional area, the

high-pressure main connected to the dynamo also being small as compared

with the distributing cable leading from the transformer, which, acting

as a step-down induction coil, converts the electricity into a safe

working pressure.

[Illustration: FIG. 9A.]

Fig. 9 A shows the arrangement of the two separate and complete

circuits. D is the dynamo, P the primary coil, S the secondary, and L

the lamps arranged in parallel.

It is hardly necessary to go into the technical details of the various

improvements which have led up to the modern type of transformers; they

are summarised by Mr. Kapp into two classes:—

I. Core transformers, one core and two sets of coils.

II. Shell transformers, two cores and one set of coils.

No. I. are those in which the copper coils are spread over the surface

of the iron core enveloping the latter more or less completely; and No.

II. in which the core is spread over the surface of the copper coils

forming a shell over the winding.

[Illustration: FIG. 10.]

The original Goulard and Gibbs secondary generator was of the core

transformer type, it had an open magnetic circuit and cores which

could more or less be inserted into the coils so as to regulate the

electro-motive force of the secondary circuit. The transformers were

constructed with a number of copper disks or washers; these were

placed alternately primary and secondary in a vertical frame, through

the centre of which an iron core was fixed, consisting of a bundle of

straight iron wires. The core was movable in the coil in the manner of

the well-known induction coils, and thereby the electro-motive force

of the secondary current could be adjusted. In their latest design

the coils are circular in plan and rectangular in section and are

surrounded by groups of U-shaped soft iron stampings slipped over from

both sides and held together by two circular cast-iron plates with a

central bolt. The magnetic lines of force pass through the core, in at

one end and out at the other, and are then more or less disseminated

through space; it will thus be seen that the path of the lines lies

partly in iron and partly in air, and, since air has about seven

hundred times more magnetic resistance than iron, it is evident that

the number of lines created with a given current must be considerably

smaller than would be the case if the path of the lines contained iron

only. This constitutes the improvement in the Zippernowsky-Deri-Blathy

system of transformer, which has coils similar to the Goulard, but with

the iron of the core applied in the form of a ring-shaped shell,

surrounding both coils completely. This arrangement can best be

described by comparing it to a Gramme armature, in which the copper and

the iron have changed places. Imagine what is usually the core in an

armature replaced by the primary and secondary coils, and, instead of

the winding of insulated copper wire, wind iron wire around the coils,

and one of these transformers is the result. In consequence of the

lower magnetic resistance of the Class II. transformer, as compared to

that of Class I., the electrical output obtainable with equal weights

of copper and iron appears to be considerably greater in the former

apparatus. Professor Feraris, of Turin, has published some of the

results of comparative experiments made with Classes I. and II. and

finds that the coefficient of induction is 3·6 times as great with the

latter as with the former. There are many varieties of transformers

in the market which closely resemble each other; one of the most

practical is that designed by Kapp and Snell, of which Fig. 10 is an

illustration. U-shaped stampings form the shell and the cores are laid

in the double trough. The cover of these troughs is formed from the

metal removed from the interior of the stampings, and the whole is held

together in a cast-iron frame so arranged as to allow air to circulate

through the core and round the coils. The price of these transformers

is about £4 per indicated horse-power, and the efficiency under the

best conditions, namely, with full load, is, according to Professor

Ayrton, as high as 96 per cent., and when it is doing one quarter of

the full work 89 per cent.

APPLICATION OF TRANSFORMERS.

The installation at the Grosvenor Gallery, London, may be taken to

illustrate Class I. or the practical working of distribution by means

of transformers.

Fig. 11 represents the arrangement of primary and secondary circuits.

An alternating current is sent through the main L L¹, which is a closed

circuit, and a small portion is drawn off wherever there is a secondary

generator or transformer T; these instruments are placed in parallel

between the conductors in the same manner as a glow lamp; neither main

can be called positive or negative, as the current flows backwards and

forwards many times in a second. The house wires M M are joined to the

secondary circuits, and are quite distinct from the main, which they

do not even touch, although sufficiently near to receive an induced

current alternating the same as the primary, but of a much lower

electro-motive force.

[Illustration: FIG. 11.

D, alternating current dynamo;

E, continuous current dynamo for exciting;

L L¹, main primary conductors;

M M, secondary conductors;

T T, transformers;

S¹ S² S³ S⁴ S⁵ S⁶, lamps in parallel.]

The Goulard transformers were used at first, but have been superseded

by others designed by Mr. Ferranti; they are of the No. 2 kind, or

shell type, and have a core of hoop-iron, on which the two coils are

wound; the hoop-iron is then bent over, and the ends joined so as to

enclose the coils. The machinery is fixed in a basement excavated under

the Grosvenor Gallery; the foundations are of massive concrete, in which

stone supports for the engines and dynamos are embedded; the concrete

does not touch the walls of the building, but a space of about 1 foot

is left, which is filled in with clay; and by this simple plan all

vibration of the machinery is isolated from the building. The power

is obtained from two horizontal high-pressure engines, each of 600

indicated horse-power, in addition to the original two horizontal

high-pressure non-condensing engines, each of 35 nominal horse-power,

running at a speed of 55 revolutions per minute, which is maintained

constant by means of a governor directly attached to the expansion

slide-valve. The four engines drive on to a countershaft, which is

cut up into lengths; each section is coupled to a dynamo and exciter

by means of a conical friction-disk clutch; this permits of either

length being started or stopped without interfering with the other. The

speed of each engine is checked by means of a liquid speed-indicator,

designed by the author. Two Ferranti alternating current dynamos,

each capable of maintaining ten thousand lamps, are driven direct,

one dynamo by each length of shafting: they are excited by two

continuous current machines, the circuits from which are joined

to a regulating apparatus, which by altering resistance keeps the

electro-motive force of the large machines proportional to the number

of lamps which are to be maintained. At present hand regulation is

employed, but it is proposed to use automatic regulation, which

will increase the life of the lamps, as they are severely tried

by the variation of the current, which is more noticeable than in

continuous current installations. The current from the machines is at a

potential of 2400 volts, and that from the transformers is 100 volts.

The primary wire which carries this high electro-motive force does not

enter the houses, as the transformers are, as a rule, fixed in the

cellars, and from them the house branch is led in the form of a cable

of fine wires, having a total diameter of 7/16 inch; the lamps, which

are placed in parallel across this cable, are attached to single No. 18

or No. 20 B. W. G. wires in the usual manner. When first established,

the transformers presented an element of danger, in that they, in

common with all induction coils, were also condensers, and therefore

a dangerous shock might be given to any one touching some unguarded

portion of the lighting system. This has been prevented by the simple

plan of connecting one of the terminals of every secondary circuit to

earth, a method which, however, is not to be recommended, as it throws

an additional strain on the insulation of the primary circuit; in fact,

by earthing the secondary the insulation is practically reduced to

one-half. A safety device should be inserted, which would come into

operation on any leakage from primary to secondary, and immediately cut

out the transformer.

The primary-current conductor is led overhead, and still remains an

objectionable feature of the system, although the original trouble

with the neighbouring telephones and telegraphs has been overcome.

The primary circuit is a small carefully insulated cable of high

conductivity copper wire, nineteen strands of No. 15 B. W. G. It weighs

about 1¾ ton per mile, and is suspended, where it crosses the streets,

on a steel bearer whose tensile strength is 1⅕ ton. It is so arranged

according to the droop of the cable that the strain of the bearer never

exceeds 225 lbs., which means that the factor of safety is nearly 12 to

1. Double cut-outs or safety fuses, in many instances of the author’s

design, are placed on each pole of the primary, at the point where

it enters the house, so that, in the case of an excess current, the

mica-foils would fuse, and all connection between that house and the

supply main would cease.

Much credit is due to M. Goulard, who, in spite of great opposition

to the use of his transformer system, initiated the Grosvenor Gallery

installation three years ago. It has developed into not only the

largest and most important central-station in Europe, but, as regards

the transformer system, it supplies more lights than any in the United

States. The original company has been taken over by the London Electric

Supply Corporation, who are putting down plant capable of maintaining

30,000 lights, and are erecting another station at Deptford for 200,000

lights, which will be distributed by means of district transformers

from mains, which it is proposed to run from Deptford through the

Thames Tunnel and the Underground Railways. The electric current is

supplied by meter at the price of 7¼_d._ per Board of Trade Unit, a

price for light equal to gas at about 4_s._ 2_d._ per 1000 cubic feet.

The Eastbourne station is also on the transformer system. An

alternating current dynamo, by Ellwell Parker, maintains a pressure

in the primary circuit of 2000 volts, which is reduced by means of a

Lowrie Hall transformer to a working pressure of 100 volts. There is a

special arrangement for maintaining a constant electro-motive force in

the mains, independent of the number of lights in use. The mains are

carried underground, and have so far given no trouble as regards the

insulation of the high-tension current which passes through them.

The Eastbourne company commenced by lighting the parade only with

arc lamps, but now supply the incandescent light to all parts of the

town, and enjoy the unique position of having obtained power from the

corporation to run the mains in the streets prior to the passing of

the Act of 1882. Another small station has been successfully worked

for the last six years at Brighton; the group system was originally

adopted, the lamps, both arc and incandescent, being placed in

series or multiple series; the high-tension current is led through

overhead wires in a very similar manner to the installation at

Temesvar, Hungary, which is described at page 58, as an example of

multiple series lighting. The extensions at Brighton are to be carried

out on the transformer plan, which will necessitate the running of

separate circuits, the intention of the company, however, being to

gradually convert its whole system of supply to the transformer system.

The Brighton Company has regularly paid dividends to its shareholders

since its formation.

*       *       *       *       *

On the Continent the Goulard transformer is largely employed.

An important installation at Tours of 3500 lamps has been for some time

successfully working. Another at Tivoli has some additional points

of interest, in that the natural power of a waterfall is applied to

generate electricity. Two turbines constructed by Escher Wyss, of

Zurich, having an available head of 29·75 feet, give 80 horse-power

each, which is employed to drive two Siemens alternating current

dynamos, separately excited by two small continuous current machines.

Two distinct circuits of chromo-bronze naked wire, 3·7 millimetres in

diameter, are run overhead, in the same manner as telegraph wires,

through the town for a total length of about nineteen miles. The street

lamps are fixed alternately on each circuit, so that one-half can be

extinguished at a late hour without interfering with the others, or

having to turn out individual lamps. The number of lamps used in the

streets is two hundred glow lamps of 50 candle-power; also one hundred

and twenty glow lamps of 16 candle-power for the illumination of the

narrower streets. Arc lamps are also employed, as well as a large

reflector lamp, the rays from which are turned on the Temples of Vesta

and Sibilla. A house-to-house system is also being established, and

the company which has put up the work proposes to utilise the falls of

Tivoli in order to transmit 2000 horse-power for lighting purposes in

Rome.

*       *       *       *       *

The firm of Ganz, of Budapest, who are the manufacturers of the

Zippernowsky-Deri-Blathy system of transformers, have a similar

installation completed in order to light a portion of Lucerne. The

water power of Thorenburg 3·1 miles off, works the turbines, which

drive two self-exciting alternating current dynamos of the Ganz type,

similar to those shown at the Vienna Exhibition in 1884. The primary

current of 38 ampères, at an electro-motive force of 1800 volts, is led

by four uncovered wires, each six millimetres in diameter, to the

first station, which is 2·4 kilometres distant; here 1500 watts are

taken off, and at 2·3 kilometres further 7000 watts are utilised in

two of the hotels at Lucerne. A large installation on the same system

has been put down in Rome, and several Continental cities are adopting

this method of supplying electric light by small overhead wires. An

advantage claimed by the Zippernowsky system is the method of keeping

the strength of the magnetic field of the dynamos in accordance with

the external demand for current. The regulating apparatus employed

consists of a small transformer, the primary coil of which is traversed

by the whole, or by a proportionate part, of the main circuit, while

the secondary coil is inserted into the exciting circuit. Thus, if

the main current increases, the exciting current induced in the two

armature coils of the dynamo is reinforced by the inductive action of

the regulating transformer; and the field of the dynamo is strengthened

when more current is required. The opposite takes place when, through

the extinction of lamps on the external circuit, the demand for current

becomes less. In an experiment made with the transformers, which

supply some five hundred electric lamps for the Teatro dal Verone

and adjoining houses at Milan from the central electrical station

three-quarters of a mile away, the main current was often found to vary

from one ampère to thirty-five ampères; it was stated that no variation

in the service pressure could be detected, and the lamps burnt with

equal brightness whatever the number in use. In the experiments at the

Teatro dal Verone each transformer worked its own independent circuit

of lamps; but, if the conditions of the different circuits were alike,

they could be coupled up together in any manner desired, and thus a

group of transformers could become a centre of distribution.

THE WESTINGHOUSE SYSTEM.

The alternating current system of the Westinghouse Company has come

to the front in the United States with extraordinary rapidity, and,

although it is not three years since the first plant was erected, at

the present time over 190,000 incandescent lamps are operated from a

number of central-stations. The fundamental principles of the Goulard

system have been retained in the Westinghouse converter; but the manner

in which these principles are applied has been greatly modified, while

most of the details have undergone a radical change at the hands of the

engineers and electricians whose researches have been utilised by the

Westinghouse Company. The form of converter as now designed consists of

a number of thin sheet-iron plates, shaped like the letter =E=, they

are slipped alternately from opposite directions over the primary and

secondary coils, which are disposed side by side; the inductive core

is, therefore, composed of a mass of detached plates insulated from

each other by paper, and forming a discontinuous magnetic circuit.

In order to protect the converter from mechanical injury as well as

dampness, and also to avoid the possibility of contact with wires

carrying currents of high potential, it is enclosed in a cast-iron case

or box, made in two parts and adapted to be secured to any convenient

support. Fig. 12 is a transverse vertical section of such a converter

box, with the converter in position. The terminals of the primary

coil, P, of the converter are led into the compartment D¹, and the

terminals of the secondary coil into D². The terminals are secured

to bolts or couplings, _f f_, mounted upon insulating plates, _e_¹

and _e_². Fusible mica-foils, _g_, and switch plates, _h_ and _i_,

with plugs _k_, are provided for protecting and disconnecting the

circuits. The open front of the compartments D¹ and D² are closed by

glass plates, T, which permit inspection of the connections without

entering the box. The converter box occupies little space, and may

be placed in any convenient situation in or about the premises to be

lighted, much the same as a gas-meter. The practice where overhead

conductors are employed, is to mount the converter box on a pole in

the vicinity of the premises to be lighted, as shown by Fig. 13, and

thus it is only necessary to lead the secondary or low potential wires

into the building, the high potential wires remaining in an accessible

position upon the pole. Fig. 14 is a view of North Street, Pittsfield,

Massachusetts, engraved from a photograph, and shows a very neat form

of tubular pole with its converter box on top. This arrangement is used

throughout the city, and is a great improvement on the ordinary form

of telegraph poles which so greatly disfigure American cities, and are

really the most objectionable feature of the overhead wire system.

[Illustration: Fig. 12.]

[Illustration: FIG. 13.]

[Illustration: FIG. 14.

_To face page 37._]

The potential ordinarily employed in the main circuits of the

Westinghouse installations is about 1000 volts, and that in the lamp

circuits 50 volts, the ratio of conversion, therefore, being as 20

to 1; the dynamos are manufactured, as a rule, in three sizes, No. 1

for 650, 16 candle-power lamps; Nos. 2 and 3 for respectively 1300

and 2500 lamps. The converters are also made in three ordinary sizes

to supply 20, 30, and 40 lamps of 16 candle-power each. A 40-light

converter contains about 85 pounds of iron and 25 pounds of copper,

so that the total weight of metal is less than 3 pounds per lamp;

the electrical efficiency of the converter is said to exceed 95 per

cent. when the potential is reduced from 1000 volts in the primary to

50 in the secondary. “It is claimed that the trifling loss of energy

in conversion from high to low potential at the point of consumption

is made up for by gain at other points, especially in the increased

efficiency of the lamps, so that an alternating current plant may be

counted on to give 10-16 candle-power lamps per indicated horse-power,

as against 7 with the direct system;” the comparative gain is doubtful,

but by using 50 instead of 100 volts the life of the lamps is

increased, the former having a much stronger filament and consequently

a longer life.

ELECTRIC MOTORS.

Having slightly diverged from the original lines by describing a system

which is at present not introduced into Europe, a few remarks on the

subject of electric motors may not be inappropriate, as they are almost

universally worked in the United States, from the installation which

supplies electric light. There is a considerable profit to the electric

company if electric power is taken in the district, the wires conveying

the lighting current are thus economically employed during the day. In

the diagram, Fig. 15, which represents a district at Boston, the curve

on the right principally represents the demand for power which takes

place between the hours of 8 A.M. and 3 P.M. A circular was addressed

to all the leading electric companies in America a short time ago,

asking if they supplied power as well as light, also for what purposes

it was used.

Answers were received from 56 companies, who stated that the motors

were employed for:—driving ventilator fans, collar-and-cuff machines,

printing-presses, various apparatus in repair-shops, sewing-machines,

coffee-mills, gun-shop tools, sausage-machines, elevators, lathes,

pumps, saws, ice-cream freezers, organ-bellows, and washing-machines.

The size of motors varied from one-eighth to 15 horse-power; 26

companies have supplied motors from arc light circuits, 14 from arc and

incandescent, and 16 from incandescent circuits alone. The motors are

principally owned by the subscribers, and are charged for at a rate

varying from £3 to £15 per horse-power per month. The motor business

is still in its infancy, but is cited to show how Electric Power can

supplant the steam-engine, especially for those purposes in which the

power required is small and complete control is desirable.

[Illustration: FIG. 15.]

CLASS II.

THE EDISON PARALLEL SYSTEM, WITH CONTINUOUS CURRENT.

It will be found, on examining Appendix II., that in European stations

by far the larger number of lamps are maintained from installations

employing the Edison system; the Ferranti plan of using transformers

comes next, closely followed by Goulard and Zippernowsky; the

distribution with secondary batteries follows, and the high-tension

multiple series comes last.

[Illustration: FIG. 16.]

The Edison system has frequently been discussed, in connection with

small installations, but in magnitude the stations in Berlin and in

Milan exceed anything that has been started here with continuous

current.

Before describing the central electric light station at the former

city, it may be well to recall to mind that the Edison plan is the

combination of a number of machines which pump electricity into a

network of feeders, mains, and conductors, the lamps being placed in

parallel circuit, as shown at L _l_, Fig. 16, and maintained at a

constant potential of 110 volts.

[Illustration: FIG. 17.]

M M′ are the flow and return mains, the dynamos bridging them across at

one end. If the mains were very long, those near to the dynamos would

be exhausting the supply, and the lamps at the remote end would not get

the full pressure. A system of feeders has been devised so that each

lamp, no matter where it may be, shall have approximately the full 110

volts working through it. Fig. 17 shows a long circuit consisting of

two branch mains bridged by a large number of lamps, _l l_, and D D are

the dynamos at the central-station. Series of feeders, _f f′_, have to

be taken from the dynamo mains and fed direct into the branch mains

at various points, _d d′_, _b b′_, _c c′_, in order to distribute the

electrical pressure equally.

THE THREE-WIRE SYSTEM.

The ordinary parallel system is undoubtedly suitable for small

installations; but when the area to be lighted is extensive, it is

impossible to proportion the mains, with a view to economy in the cost

of copper, without sacrificing energy wasted in heating the conductors.

In Figs. 16, 17, the lamps are shown in simple parallel; but if two

dynamos are connected together, and a main wire is run from each of

their two extreme terminals and a third wire from the branch connecting

the two machines, we have what is known as the three-wire system,

which was invented by Edison in America, and Hopkinson in England,

almost simultaneously. Although by using the third wire there is a

saving in copper over the parallel plan, the maximum gain is not more

than 25 per cent., under the best conditions; when the district to be

illuminated is not more than 400 to 600 yards from the central-station,

the three-wire system answers well, but as soon as this distance is

exceeded the cost of the mains begins to mount up at a most alarming

rate. Although there are many Edison installations in the United States

on this system and a few on the Continent, it has only been used here

in a few instances for factory lighting.

THE EDISON SYSTEM AT MILAN.

The Santa Radegonda station at Milan is at the present moment the

second largest Edison station in Europe. The building, which was

formerly a theatre, is well adapted for the work required; the dynamos

and engines are fixed in a deep basement, while the boilers are a few

feet above the street level, the upper floors being used as stores and

testing-rooms. The dynamos, eight in number, are of the old Edison

type, with horizontal magnets; seven of these machines are connected to

the feeders which supply the mains, and these cover the district to be

lighted on the Edison network system. The motive power is furnished by

six Armington-Sims, and two Porter-Allen engines, each connected direct

to the armature of a dynamo, the speed being maintained at the uniform

rate of 350 revolutions per minute, except in the case of the spare

engine and dynamo, which is kept turning slowly, ready to be switched

on should occasion demand. The starting or cutting-out of circuit of

these large machines requires some care. In the first place, to start,

it is necessary to insert resistance into the shunt circuit of the

dynamo, which is done by a switch; but to throw 150 horse-power into

the main circuit would be dangerous to the lamps, so that the current

is first sent into a bank of one thousand lamps used as a resistance,

and these are cut out step by step; similar care is taken when a

machine is stopped. To control the electro-motive force, which varies

greatly from time to time, hand regulation is used during the day, with

the help of the Edison tell-tale, consisting of two lamps, a red and

white one, which light up when the current is high or low; but when the

night service comes on, as it may happen that two thousand lamps may be

turned out at once, an attendant has to carefully watch the electric

regulator, and be ready to insert resistance into the field-magnet

circuits by moving a wheel connected by a shaft and bevel-gear to a

system of commutators. The principal difficulty to be overcome, in

an installation where the current is distributed over a large area,

is the regulation of the electro-motive force at the various points,

as at Milan; there are no return galvanometer wires, which are now

used in both the two and the three-wire Edison systems in the United

States. The plan devised by the company’s electrician at Milan is very

ingenious, and enables the pressure at the ends of the various feeders

to be kept practically the same, although they are of different lengths

and sectional area. In the first place, resistance was added to each

feeder to equalise the resistance in each conductor; and, in order to

provide for the varying amount of current the feeder has to supply, a

peculiar form of commutator, having a guillotine-shaped contact-piece,

was inserted in the circuit. By moving this, suitable resistance is

inserted or cut out, and the attendant, having a series of numbers, has

only to set this instrument to the number shown by the ampère meter. By

far the largest amount of current is drawn off for the lighting of the

Scala Theatre, the stage-lighting alone taking more than one thousand

lights: if these were all turned on suddenly, the other lights in the

district would be dimmed; to obviate this, auxiliary feeders have been

run, which are used only when any great increase is expected;

commutators similar to those referred to above also regulate these

feeders without any special attention. The pressure at any point in the

system is by this means easily controlled, and affords an illustration

of what is perhaps not the most economical, but is found to be the most

practicable, way of maintaining a constant potential in a district

where the amount of output of current is suddenly doubled. Fig. 18 is a

plan of the network system of conductors laid through a large portion

of the city; the conductors are in outward appearance similar to

gas-pipes, the current passing through semicircular bars of copper,

embedded both for the flow and return in the same iron tube, which is

laid underground in a shallow trench. The house-supply is drawn from

the mains, and these are connected to the feeders by means of ordinary

junction-boxes, which each contain a fusible cut-out. The bridge-boxes

allow of expansion of the line, and have connections for testing

purposes. The insulation is extremely good, mainly on account of the

favourable nature of the ground, which is chiefly gravel; no trouble

has been experienced with leakage, nor has the service ever been

interrupted. The cut-outs are of an improved Edison form, but have the

disadvantage attending all lead plugs where the current is great, in

that, to guard against accidental melting due to the heating effect of

the current, the sectional area of the lead has to be much larger than

would be otherwise necessary. In fact, these cut-outs will protect the

cable against a bad short circuit, but nothing else.

[Illustration: FIG. 18.]

In addition to the glow lamps, eighty arc lamps are worked in

derivation, two in series; most of these lamps require 45 volts,

to which 10 per cent. of idle resistance is added, constituting a

total loss of current which is extremely low for a combined arc and

incandescent system of lighting. The service commenced in 1882 with

a little over one hundred lamps, and at present there are over ten

thousand glow lamps, and two hundred arc lamps are in use. At first the

new enterprise had to struggle against very great difficulties; not

only the technical difficulties of distribution by means of a network

of feeders and mains had to be overcome, but also those arising from

the prejudices of consumers and the competition of the gas company,

who tried to deter consumers from introducing electric light into

their houses. One of these means consisted in offering to the private

consumers, resident in the district which was threatened by competition

with electricity, an agreement by which the gas company bound itself to

supply gas at 5_s._ 8½_d._ per 1000 cubic feet, instead of 7_s._ 7_d._

as charged hitherto; and even now those inside the “charmed circle” of

the electric light conductors get their gas cheaper than the public

outside. One of the reasons which accelerated the adoption of electric

light was the introduction of the Edison meter, in consequence of which

consumers could be charged exactly for the amount of light they had

received, and were relieved from paying a lump sum according to the

number of lamps fixed, which was customary in the early days of the

company. The prices at which the company now provides light, at all

hours of the day and night, are as under:—

Installation      Charge per

Type of Lamp.    charge per lamp.    lamp·hour.

_s._              _d._

10-candle               18              0·26

16-  ”                  28              0·40

32-  ”                  56              0·80

that is, a little over ½_d._ per ampère-hour; the 10-candle lamps

requiring 0·5, the 16-candle lamps 0·75, and the 32-candle lamps 1·5

ampère.

The company lends meters for 50, 100, and 150 lamps, at an annual

rent of 4_s._ 10_d._, 7_s._ 3_d._, and 9_s._ 7_d._ respectively, and

replaces, without charge to the consumer, any lamp the filament of

which has broken, but it does not replace lamps where the glass is

broken. For arc lamps requiring 9 to 10 ampères, an annual rent of £2

must be paid for the lamp itself, and a charge of a little over ½_d._

per hour for every ampère-hour. The carbons are charged for at 1_d._

per pair, lasting for about seven hours. Now that the installation has

been in use for several years, and that the company has arrived at a

very accurate estimate of the time during which an average consumer

requires the light—about one thousand six hundred lamp-hours per

annum—it proposes to simplify the method of charging large consumers,

by omitting the initial charge of each lamp, and, instead, to charge

0·6_d._ for each 16-candle lamp-hour.

The Edison meters are based on the electrolytic action of a small

fraction of the current which passes through the meter. They are cells,

with rectangular zinc plates immersed in a solution of sulphate of zinc

of 1·054 density, the distance between the plates being a little over ¼

inch. The proportion of the current which passes through the meter to

that which passes directly into the consumer’s house is 1 to 973. The

resistance of the shunt circuit is 9·75 ohms, made up as follows: cell,

1·75 ohm; metallic portion, 8 ohms. The resistance of the metallic

portion rises with the temperature, whereas that of the cells falls

with a rising temperature; and in this manner the small variations of

resistance which might take place in the cell are counter-balanced

by the equally small variations in the resistance of the metallic

portion. A complete meter consists of two similar-sized cells of the

same resistance, placed in series. The object of employing two cells

is, that when little current is passing, as in the summer months, one

cell alone is used, and when the consumption is sufficiently large both

cells are employed, and the mean between the two indications is taken

as the basis for calculation in number of ampère-hours. The quantity of

electricity passed through the cell is calculated by the loss of weight

which has taken place in the positive plate. An employé of the society

visits every meter monthly, taking away the old cells and substituting

others freshly constructed. A book is kept in which the weights of the

new plates and those of the returned plates are entered, and on the

basis of these entries the accounts are made up. The largest plates are

those in the 100-light meter, and are intended for a maximum current

of 75 ampères in the main circuit; they are 6 inches long by 2 inches

wide. In cases where a larger amount of current is taken, the capacity

of the 100-light meter is increased by joining two or more copper

strips across the terminals of the cells. The weak point of the system

is the removal of the cells, which leaves the adjustment of the account

to be paid entirely in the hands of the Electric-Light Company; in

spite of this drawback, it is stated that there has not been a single

complaint from consumers during the four years in which the meter

system has been in use.

_Discovery of Faults._

It is evident that in so extensive a system of lighting a short circuit

now and then between the lamp wires and the earth cannot altogether be

avoided. Many of the lamps have been fitted to existing gas fittings,

and are beyond the daily supervision of the company’s officers; the

faulty place is often not easily accessible, so the first step taken is

to discover on which of the two circuits the trouble has occurred. This

is done at the station by joining two 16-candle lamps in series across

the main conductors and the point of junction between the two lamps is

connected to earth by a stout wire. As long as both circuits (positive

and negative) are perfectly insulated from earth no current flows

through this middle wire, and both lamps remain hardly incandescent;

but, if one of the circuits should be in connection with the earth, the

lamp which is joined on the other circuit will brighten up, because the

potential of the middle wire and that of the faulty circuit are both

zero, and consequently the lamp between the middle wire and the sound

circuit receives the full pressure of 110 volts. To localise the fault,

contact is made between the earth and the sound circuit by means of a

fusible plug of known melting point, say for a thirty-lamp supply. If

the fault is on a portion of the external circuit, supplying less than

thirty lamps, its fusible plug will melt as soon as the sound main is

put to earth. If, however, the fault is on a portion supplying more

than thirty lamps, the fusible plug which has been inserted at the

station between the sound main and the earth will melt instead. A

series of fusible plugs are thus tried, increasing in melting capacity

until one is found that does not go: in this case, the other plug on

the faulty portion has melted, and the consumer’s lamps on that branch

are extinguished; the position of the fault is thus localised, and

the company proceed to remedy the defect without interfering in the

slightest degree with the rest of their system.

THE ELECTRIC LIGHTING OF BERLIN.

The Edison system is also employed at Berlin, in fact the Deutscher

Edison Gesellschaft have at the present time a monopoly of the supply

of the city from three large central-stations, each of which serves

the area in their immediate neighbourhood. The mains differ from those

used at Milan in that stranded highly insulated cables, protected

with steel wire on the outside, are laid under the pavement in every

street throughout the district. With the exception of the Leipziger

strasse and Unter den Linden, which are lit with arc lamps suspended

from chains running between cast-iron poles 24 ft. high, about 100 to

250 ft. apart, gas is used for the street lighting, and electricity

for the interior illumination of many public buildings and private

houses; there are also a good many arc lights outside the shops and

restaurants. The mains are on the Edison network system, the area of

copper being such, that when all the lamps are on there is a loss of

energy of 25 per cent.; but this does not occur on an average for more

than half an hour a day. No sole concession is given to the company,

who simply have the right to take up the pavement and cross streets,

and for this permission they are bound to furnish any consumer in

the district with a constant supply of electricity at the following

charges:—

10-candle lamps 2·5 pf., about 0·29 _d._ per hour.

16-      ”      4·0        ”   0·48       ”

32-      ”      8·0        ”   0·96       ”

50-      ”     12·5        ”   1·50       ”

100-      ”       25        ”   3·00       ”

In addition to this an installation fee of 6_s._ per lamp is charged,

which includes one lamp.

Meters are charged as follows:—

_£   s.   d._

10- to 16-candle-power   0   16   0 per annum.

25-    ”       ”         1    0   0     ”

50-    ”       ”         1   10   0     ”

100-    ”       ”         2    0   0     ”

A discount is allowed off this meter charge, varying with the number of

hours the light is used in the year.

The cost of gas is about 4_s._ 9_d._ per 1,000 cubic feet, so the

electric light is slightly the dearer illuminant.

The Aron meter, Fig. 19, is usually employed as the recorder of the

electricity consumed. It consists of two pendulums, controlling two

distinct clockwork gears. One oscillates at a regular speed, but the

other has a permanent magnet, instead of a weight, and is variable in

speed. The entire current passes through the solenoid, which is

underneath the pendulum, with the magnet; the difference in speed

between the standard and variable clocks is given in direct

ampère-hours by a counter-gearing similar to the index of a gas-meter.

An electro-magnet starts each pendulum when the current begins to flow,

and immediately it ceases, two detents come into operation and hold the

pendulums stationary.

[Illustration: FIG. 19.]

CLASS III.

THE SERIES SYSTEM OF DISTRIBUTION.

This method dates back to the introduction of the incandescent light,

and, although it has been frequently demonstrated that a small current

of high potential could be employed to work incandescent lamps, the

series system has never been installed on a commercial scale, and is

confined to arc lighting. In the United States the usual pressure for

arc lighting is 2,000 volts, and it is not an uncommon occurrence to

have forty arc lamps in series upon a line over 10 miles in length,

carrying a current of 10 ampères. To economically use this high

pressure for glow lamps in series, they must be of such design as to

enable the whole of the current to be passed through them without

injury. The filament of an ordinary high-resistance glow lamp would

be immediately destroyed, so that low-resistance lamps, having a much

larger sectional area, must be employed. The Bernstein or the Cruto

lamp, which can be made to have a “hot” resistance of about 0·7 ohm,

and requires a current of 9·75 ampères, could be used, and the current

might be economically brought from a great distance. Mr. Bernstein

calculates that it would be possible to operate 6,000 of these 7-volt

lamps from twenty dynamos, each giving a current of 10 ampères at

a potential of 2,000 volts, and still have a margin for loss of

current in the leads. An economical feature of this scheme is the

easy way in which power could be saved when only comparatively few

lights were required; for instance, in the daytime all the circuits

could be looped together and fed by one dynamo, and, as the number of

lights increased, so other machines could be switched in by having

an auxiliary bank of lamps as a resistance. From the central-station

twenty pairs of carefully insulated copper wires, say of No. 6 B. W.

G., would lead to the houses; and, as a good-sized ordinary house takes

on an average twenty lights, the conductor would pass through fifteen

houses before it returned to the station. It is in the house that the

practical difficulty commences, as in this series system the circuit

must never be opened, so that the switches and safety appliances must

be such that, whatever happens, there must remain some path for the

current, otherwise all the lights on that particular circuit would be

extinguished. Mr. Bernstein gives the designation of “short closed” if

the current goes through the switch-lever, and “long closed” if the

current is led through the lamps or other electrical devices.

[Illustration: FIG. 20.]

Fig. 20 is a diagram of the lamps in any building. The street main, M,

enters at the main switch, S, and continues from switch to switch, S¹

S¹, and returns to S before it leaves. It is necessary, to guard

against any possible extinction, to construct all the switches so that

it would be impossible to move the lever without a lamp was lighted;

and, should the lamp give out, an equivalent resistance must be

automatically inserted. These details have been investigated by Mr.

Alexander Bernstein, who has designed a complete system for “series”

lighting, and claims for it special economical advantages. It is,

however, very doubtful if this plan can be recommended for adoption

in private houses; but in public lighting, or in large establishments

where an electrician could be kept to look after the fittings and

the insulation of the conductors, there should be no more danger, in

introducing the high-tension continuous current of 2,000 volts, than

there is at present with the 100-volt alternating current, and the

relative saving in weight of conductors would be an important item.

Installations on this method have been erected at Messrs. Brunner and

Mond’s alkali works, and in several large factories in the United

States where lights had to be distributed over a considerable area; the

system has not, however, come into favour for central-station work.

CLASS IV.

THE MULTIPLE SERIES SYSTEM.

This method of using a high-tension current has already been referred

to in connection with house-to-house lighting at Brighton, it was first

employed for the street lighting of Chesterfield by the Brush Company.

The electric lighting of the town of Temesvar, in Hungary, is on a far

larger scale, and has, from November 1884, successfully superseded a

combination of gas for the more important streets, and petroleum for

the outlying ones, the total cost of which was 26,480 florins per

annum. A twenty-four years’ concession was given to the International

Electric Company, the plant remaining their property at the expiration

of the term, subject to purchase by the municipality at their own

valuation. The public lighting is stipulated to be effected by means of

731 glow lamps of the intensity of 16 candle-power; but the option is

given to the company of switching out a fixed proportion of these lamps

at 11.30 P.M., or of leaving the whole number in operation

with their light-intensity reduced from 16 to 8 candle-power from 11.30

P.M. till dawn. The total number of lighting hours per annum

is 3,597½ for the lamps which are in operation from dusk until dawn,

and 1,816 for those which are extinguished at 11.30 P.M. The

price fixed in the concession for public lighting is 1·5 kreutzer per

16 candle-power lamp per hour, equal to 53 florins 95 kreutzers per

lamp per annum of 3,597½ hours, or 27 florins 24 kreutzers per lamp

per annum of 1,816 hours. The company has found it more convenient

to exercise the option reserved to it, of keeping all the 731 lamps

in operation from dusk till dawn, reducing their light-intensity to

8 candles after 11.30 P.M.; and the municipality has agreed

to pay a round sum of 29,000 florins (£2,416 13_s._ 4_d._) per annum

for this lighting, and 41·95 florins (£3 10_s._) per annum for each

additional lamp worked in the same way. Comparing these figures with

what precedes, it will be found that the electric lighting of the

streets now in operation costs 2,520 florins more than it did on

the former plan of combined lighting, partly by gas and partly by

petroleum. On the other hand, the streets are lighted throughout with

16 candle-power lamps from dusk until 11.30 P.M., and with 8

candle-power lamps from 11.30 P.M. until dawn. For electric

light supplied to private consumers the concession fixes the price at

1·81 kreutzers per 16 candle-power lamp per hour, or 0·1131 kreutzers

per candle per hour, with the right to charge 15 per cent. more for

lamps of less intensity than 16 candles. In all these prices the

renewal by the company of lamps failing from legitimate wear is

included.

[Illustration: FIG. 21.

MULTIPLE SERIES LIGHTING. TEMESVAR.]

One central generating station has been provided for the whole town,

from which at present four distinct circuits have been laid, each fed

by a separate dynamo. The street lamps are connected up in “multiple

series,” that is to say, in groups placed in series on the circuit, the

lamps in each group being connected up in parallel.

Fig. 21 shows the arrangement diagrammatically. Each group consists

of eight lamps in parallel; at present three of the circuits have

twenty-four groups in series, and the fourth circuit has twenty-three

groups in series, giving a total of ninety-five groups, comprising 760

lamps, of which 731 are public lamps and 29 are used at the central

station. To meet the risk of interruption in any circuit through

the failure of individual lamps, an automatic switch is arranged so

as to put in a reserve lamp, in the event of a whole group being

interrupted. Another self-acting device will short circuit the whole

group, so that the other groups in the circuit will be unaffected. The

automatic lamp-switch is contained, together with the reserve lamp,

in the lantern, and the automatic group cut-out consists simply of an

electro-magnet with a coil of high-resistance connected up in parallel

with the group of lamps it protects. These appliances have been found

to work well. The main conductors are formed of insulated single

copper wire, 4·6 millimetres in diameter; they are carried overhead on

porcelain insulators, fixed to telegraph posts or to wooden arms let

into the walls of houses; the resistance of this conductor is about 1·1

ohm per kilometre. The glow lamps are placed in reflectors at an angle

of about 45° from the vertical, and are carried on brackets either

fixed to the walls or on special cast-iron posts. Fig. 22 shows the

details of street bracket and reflector with automatic lamp-switch and

lamps in place. The brackets are for the most part fixed to the walls

of houses or to painted wooden posts.

[Illustration: FIG. 22.

LAMP BRACKET.]

The under side of the reflector, which is made of enamelled iron

disposed in the form of a flat inverted cone, reflects the upward

rays from the lamp and causes the extreme ones to strike the ground

at a distance of about 50 metres from the foot of the lamp-post. The

increase of lighting effect in the streets due to those reflectors

is very marked. The upper part of the reflector serves the purpose

of a case and weather protector for the automatic lamp-switch which

is inserted from the top, and the lower end of which is fitted with

copper hooks to which the two lamps are fixed. The glow lamps are

fitted with holders of a type designed by the engineer, which provide

the lamp terminals with large and strong eyes affording considerable

contact surface and adapted for hooking on direct to 2·5 mm. copper

wire, the ends of which have merely to be bent into a suitable form for

maintaining the lamp in any required position. These lamps are of an

improved Lane Fox type, manufactured by the Electrical Company, at

their works in Vienna. Although originally intended for 16 candle-power

lamps they have so far been worked at 18 candle-power, taking 53·618

volts and about 1·183 ampères, which is equivalent to 3·522 watts per

candle-power, or about 211 candles per horse-power. The current is

maintained at 10 ampères, and the potential between independent groups

of lamps is 53·6 volts. The aggregate energy lost, in overcoming the

resistance of the main leads, switches and cut-outs, is 12·8 per cent,

of the total electrical energy generated at the central-station—a

very satisfactory result on a system of over 37 miles of streets. The

electro-motive force in the conductors is about 1,400 volts, which is

below the normal capacity of a Brush machine, thus allowing more lamps

to be operated from the four machines. The machinery is driven by a

300 horse-power horizontal compound-condensing tandem steam-engine,

running at the normal speed of 100 revolutions per minute. During the

first 1,200 hours of lighting, only three lamps out of 760 failed, and

one of these had been broken maliciously. The engineering arrangements

are due to Mr. C. F. de Kierskowski Steuart, M. Inst. C.E., the

various difficulties incidental to a novel work having been surmounted

with experienced workmen. Although the system at Temesvar has more

complicated arrangements than are now required if secondary generators

are used, it has shown that it is quite practicable to light all the

streets in a town by electricity; also it has enabled a comparison to be

made between the useful effect obtainable from arc and from glow

lamps. Each group of glow lamps was found to absorb practically the

same energy as one arc lamp of from 800 to 1,000 candle-power, and

ninety-one or ninety-two of these could have been run with the same

expenditure of power as 731 glow lamps. The eight glow lamps forming

one group are in many cases scattered in different streets, often quite

out of sight of each other. Under such circumstances, the substitution

of one light centre, however powerful, for every eight could only be

done by leaving many spots in complete darkness. To give a usefully

diffused light by means of arc lamps, their number would have to be

considerably greater than ninety-two, or, in other words, the standard

of street lighting would have to be raised, and for this the town was

not prepared to pay.

The business has now passed into the hands of the Anglo-American

Corporation of London, who are extending the installation by placing

alternating current dynamos at the station to work transformers for

the supply of houses so as to utilise the original plant for street

lighting only, as, even with the advanced knowledge of the present day,

it is doubtful whether for this purpose a more economical system could

be employed.

CLASS V.

THE DISTRIBUTION WITH SECONDARY BATTERIES, OR THE BATTERY TRANSFORMER

SYSTEM.

Mr. Lane Fox was the first to put forward a complete system of

electrical supply on this plan, Fig. 23.

[Illustration: FIG. 23.

G Generating station.   A Accumulators (secondary batteries).

R Returns.              M Mains or conductors.

L Lamps.                X Meters.

]

The system is discussed by him as follows:[4]—

“The chief points of the system is the use of a generator in a central

position, from one pole of which insulated conductors or mains are led

to the several points where the electric energy is to be utilised,

being branched and sub-branched as much as required, and thence back

to the other pole of the generator by an uninsulated conductor, such

as the gas or water pipes. At certain points, storage or secondary

batteries are set up in connection, on one hand, with the mains,

sub-mains, and branches, as the exigencies of the case may require,

and, on the other, with the return conductor.”

[4] Hedges on the Supply of Electricity by Local Authorities.

Proceedings of Association of Municipal and Sanitary Engineers and

Surveyors, vol. ix. (1882-83), p. 159.

“The combination of generators, circuit and storage batteries is such,

that when the current from the generators falls below the demands made

on it from the various outlets to the mains at which its energy is

utilised, the deficiency is made up from the storage batteries, which

act in unison to supply the requisite quantity of energy. On the other

hand, when the current from the generator exceeds in point of quantity

the demands upon it at the various outlets, the excess goes to charge

the storage batteries and to create a reserve to be called upon in case

of need.”

The objection to the system which prevented it being put in practical

operation was the use of the earth as a return conductor. Besides the

great danger of short circuit, the gas and the water pipes, which

are so thickly laid in most cities, would conduct the current and

interrupt telegraphic and telephonic communication. The experiment of

using storage batteries as reservoirs, from which a constant supply of

electricity could be drawn as required, was tried on a considerable

scale at Colchester, where a large installation was started in 1884,

secondary batteries being placed in favourable positions, and charged

by a high-tension current. The plan adopted is shown by Fig. 24.

[Illustration: FIG. 24.

A is a meter in charging circuit; B, the batteries or accumulators; L,

lamps in parallel on low-pressure service main.]

The dynamos were two of the Brush type, each dynamo giving a current

of 9·5 ampères, with an electro-motive force of 1,800 volts, when

rotated at a speed of 700 revolutions per minute. They were driven by

a semi-portable engine indicating 90 horse-power. The dynamos were

coupled in parallel circuit for quantity, and excited by a small

machine giving 10 ampères. The current was led some distance by a

seven-strand 19 B. W. G. cable to the batteries, which were charged in

series, the 60-volt lamps being placed in parallel on separate mains

connected to the batteries. The danger of introducing a high-tension

current of 1,800 volts into the houses was obviated by a rocking-switch

worked automatically, so as to throw the batteries out of the charging

circuit. The operation was accomplished by means of a master cell M,

C, Fig. 24, similar to the others, but fitted with an arrangement

to collect the gas evolved, which extended a diaphragm attached to

a make-and-break arrangement which worked the rocking-switch. The

Colchester installation did not turn out commercially successful, and

has been abandoned; but the experiment has been valuable, and there

is little doubt that, with simplification of details, a high-tension

charging current could be led from a dynamo fixed in any convenient

site where power is available; also in very crowded districts the

batteries could be placed in cellars and be drawn from as reservoirs,

so as to furnish a constant supply of electricity.

[Illustration: FIG. 25. _To face page 69._]

The Kensington Court installation has been previously quoted as an

example of what promises to be one of the most successful methods

of distributing a constant supply of electricity through a large

area, a description of the station may therefore be interesting. The

accompanying elevation, Fig. 25,[5] shows the unpretending design

of the building, and the very compact arrangement of the generating

machinery and batteries. When the illustration was made the plant

consisted of one Willan’s single-crank triple-expansion engine in

combination with a Crompton dynamo provided with vertical inverted

single magnets, the output being 250 ampères at 140 volts when running

at 500 revolutions per minute, the steam pressure being 160 lbs. on the

square inch. A complete duplicate plant has already been installed, and

three more sets of engines and dynamos are shortly to be erected. The

draught from the boiler is led downwards by an underground flue, with

the object of economising the very limited space as much as possible.

As a rule, the dynamo and accumulators are used in parallel, the

current enters and leaves the regulating cells by the same contact,

in other words, there is only one switch which serves for charging

and discharging the batteries. This switch has nine contacts, so as

to give nine degrees of regulation of the light; when the dynamo and

accumulators are working together, the lights are parallel with either

41, 42, or 43 cells, according to the amount of charge in the cells and

current required, while, when the dynamo is out of circuit, the lights

are worked off, 50, 51, 52, or 53 cells. The current passes through the

usual measuring instruments, and each main conductor is protected by

safety fuses mounted in a Hedges duplex cut-out. The accumulators are

of the Planté type, but instead of being plain lead are sawn out of

ingots which are cast porous on the Howell process. Each cell contains

35 plates, 8 in. × 8 in., and, as each plate when fully formed is said

to be capable of yielding five ampère-hours per pound of lead, the cell

has about 600 ampère-hours total capacity. In the event of a serious

breakdown the whole of the work would fall on the accumulators, which

could furnish a steady current for perhaps an hour or more; and herein

lies the novelty of the arrangement. For the first time we have an

accumulator put in not only as a fly-wheel to the whole system and

to give the advantage of supplying current throughout the day and

the small hours when the engine is not running, but also to act as

an actual reserve. The routine is as follows:—the dynamo will start

charging the accumulators a few hours before dusk; for a short time

after lighting hours commence, the dynamo alone will supply sufficient

current, but later on the demand will gain on the dynamo, and a certain

portion of the discharge will be from the accumulators. At eleven

o’clock at night the engine will be stopped and the accumulators will

alone supply the demand for the rest of the night. In the small area

occupied by the station there is ample room for a plant of six times

the present capacity, and it is intended to erect sub-distributing

stations at points at the outskirts of the district where accumulators

to act as transformers will be fixed, which will be charged by a

special main with a current of 500 volts, the outgoing wires from the

sub-station taking electricity at the usual E.M.F pressure for

incandescent lamps in houses of 100 volts.

[5] From _Industries_.

Thirteen candle lamps are used in the district, having been found to be

more convenient than 16 or 20 candle-power, the 13 candle is obtained

for 36 watts, or 2·75 watts per candle. The price charged to consumers

is 8_d._ per Board of Trade unit, or equivalent to gas at about 4_s._

7_d._ the 1,000 cubic feet. Meters on the Aron plan, Fig. 17, are

used, a card being supplied on which the readings are entered exactly

similar to the method adopted with gas. The service mains terminate at

the meter, where the company fix for their own purposes a double pole

switch of the author’s design, Fig. 26, which enables both wires to

be disconnected, a spring shut-off, marked S S, prevents the

switch being left partly on.

SYSTEM OF DISTRIBUTION.

The mains from the Kensington Court Station are laid underground in

a culvert 18 in. by 12 in., which is built with brickwork and cement

under the pavement. A double conductor of flat copper, 0·25 square

inches section, is stretched from shackle insulators attached to iron

bars, which are firmly built into the culvert; the continuity of the

circuit is provided by means of stranded wire, which connects each

section; the flat copper rests on the top of porcelain insulators,

fixed on vertical iron pieces, which are built into the floor.

Connections with the sewers are left for drainage, and six surface

boxes are provided for every hundred yards. Where house connections

have to be made, the branch wires are united by soldering to the bare

copper mains. For crossing under the streets a heavily insulated cable

is employed, and is led through cast-iron pipes.

[Illustration: FIG. 26.]

Until a larger amount of mileage is actually at work, it is difficult

to express an opinion as to which is the cheapest and most efficient

method of laying conductors in the streets. The relative cost of two

plans tried at Kensington Court—the insulated and the bare cable in a

culvert—was given by Mr. Crompton in the following Tables, No. 1 and

No. 2, which are taken from a paper read before the Society of

Telegraph Engineers and Electricians on April 12th, 1888.

Table No. 1 refers more particularly to what is known as the

Callender-Webber system of using bitumen concrete, which is compressed

into blocks or cases usually about 6 ft. long, 8 in. by 5½ in. section,

having two-inch holes through which the insulated copper cable is led.

The estimates given in Table No. 2 were criticised by Mr. Kapp, who

thought that “a more reliable conductor could be obtained by using a

high-class lead-covered cable, which might be laid in the ground with

the simple protection of a rough tarred plank to cover it.” The cost of

digging the trench and running in the cable from the drum was quoted at

3_s._ a yard, and the total cost, inclusive of £10 for surface boxes,

at £155 per 100 yards, instead of £187, as shown by the Table.

TABLE I.

_Cost of Laying 100 Yards of Double Conductor underneath the Footway

of a London Street._

-------------------------------+---------+--------+--------+

| Single. |  7/16  | 19/15  |

| No. 16. |        |        |

-------------------------------+---------+--------+--------+

Area, square inch              |  ·0032  | ·0225  |  ·0773 |

Area, square millimetre        |  2·08   |  14·6  |    50  |

Weight per 100 yards run   lb. |   7½    |  53½   |   183¼ |

Cost of copper at 7¾_d._       |£ 0  4 10| 1 14  6| 5 18  0|

Cost of insulation             |  1  3  2| 4  8  6|11  2  0|

+---------+--------+--------+

Total cost of Cables     |  1  8  0| 6  3  0|17  0  0|

Casing, bitumen, and cement    |  5  3  0| 5  5  0| 8  0  0|

Labour, Laying                 |  3  0  0| 4  0  0| 5  0  0|

Trenching and repairing        | 25  0  0|25  0  0|25  0  0|

Surface boxes and connection   |  5  0  0| 7  0  0|10  0  0|

Engineer and superintendent    |  3  0  0| 4  0  0| 5  0  0|

+---------+--------+--------+

Total                    |£42 11  0|51  8  0|70  0  0|

Add extra if copper, at        |         |        |        |

9½_d._                       |  0  1  1| 0  8  0| 1  7  0|

+---------+--------+--------+

| 42 12  1|51 16  0|71  7  0|

Cost of copper per lb.,        |         |        |        |

laid complete                |  5 13  6| 0 19  4| 0  7  9|

Current in ampères             |   1·2   |  8·1   |   28   |

Cost per ampère                | 35 10  0| 6  8  0| 2 10  6|

-------------------------------+---------+--------+--------+

-------------------------------+--------+---------+

| 19/12  |  19/10  |

|        |         |

-------------------------------+--------+---------+

Area, square inches            | ·1613  |   0·25  |

Area, square millimetres       |   104  | 161·25  |

Weight per 100 yards run   lb. |   392  |   576   |

Cost of copper at 7¾_d._       |12 13  0| 18 15  0|

Cost of insulation             |24 17  0| 35 17  0|

+--------+---------+

Total cost of Cables     |37 10  0| 54 12  0|

Casing, bitumen, and cement    |12 10  0| 12 10  0|

Labour, Laying                 | 5  0  0|  6  0  0|

Trenching and repairing        |25  0  0| 25  0  0|

Surface boxes and connection   |10  0  0| 10  0  0|

Engineer and superintendent    | 5  0  0|  6  0  0|

+--------+---------+

Total                    |95  0  0|114  2  0|

Add extra if copper, at        |        |         |

9½_d._                       | 2 17  0|  3  5  0|

+--------+---------+

|97 17  0|117  7  0|

Cost of copper per lb.,        |        |         |

laid complete                | 0  5  0|  0  4  1|

Current in ampères             |    58  |    90   |

Cost per ampère                | 1 13 9 | 1   6  0|

-------------------------------+--------+---------+

-------------------------------+-------------+-------------+

|   37/10     |  Two Sets.  |

|             |    37/10    |

-------------------------------+-------------+-------------+

Area, square inches            |    0·5      |    1·0      |

Area, square millimetres       |    322      |    645      |

Weight per 100 yards run   lb. |    1153     |    2306     |

Cost of copper at 7¾_d._       |  37  5  0   |  74 10  0   |

Cost of insulation             |  70 15  0   | 141 10  0   |

+-------------+-------------+

Total cost of Cables     | 108  0  0   | 216  0  0   |

Casing, bitumen, and cement    |  16  0  0   |  22  0  0   |

Labour, Laying                 |  10  0  0   |  18  0  0   |

Trenching and repairing        |  25  0  0   |  25  0  0   |

Surface boxes and connection   |  10  0  0   |  10  0  0   |

Engineer and superintendent    | 10  0  0    |  10  0  0   |

+-------------+-------------+

Total                    | 179  0  0   | 301  0  0   |

Add extra if copper, at        |             |             |

9½_d._                       |   8 10  0   |  17  0  0   |

+-------------+-------------+

| 187 10  0   | 318  0  0   |

Cost of copper per lb.,        |             |             |

laid complete                |   0  3  3½  |   0  2  8¾  |

Current in ampères             |     180     |    360      |

Cost per ampère                |   1  1  0   |   0 17  6   |

-------------------------------+-------------+-------------+

-------------------------------+-------------+-------------+

|  Four Sets. |  Six Sets.  |

|    37/10    |   37/10     |

-------------------------------+-------------+-------------+

Area, square inches            |     2·0     |     3·0     |

Area, square millimetres       |    1290     |    1935     |

Weight per 100 yards run   lb. |    4612     |    6918     |

Cost of copper at 7¾_d._       | 149  0  0   | 224  0  0   |

Cost of insulation             | 283  0  0   | 424  0  0   |

+-------------+-------------+

Total cost of Cables     | 432  0  0   | 648  0  0   |

Casing, bitumen, and cement    |  40  0  0   |  55  0  0   |

Labour, Laying                 |  35  0  0   |  50  0  0   |

Trenching and repairing        |  30  0  0   |  35  0  0   |

Surface boxes and connection   |  10  0  0   |  10  0  0   |

Engineer and superintendent    |  20  0  0   |  25  0  0   |

+-------------+-------------+

Total                    | 567  0  0   | 823  0  0   |

Add extra if copper, at        |             |             |

9½_d._                       |  34  0  0   |  51  0  0   |

+-------------+-------------+

| 601  0  0   | 874  0  0   |

Cost of copper per lb.,        |             |             |

laid complete                |  0  2  7¼   |  0  2  6¼   |

Current in ampères             |    720      |   1,080     |

Cost per ampère                |  0  16  8   |  0 16 1     |

-------------------------------+-------------+-------------+

TABLE II.

_Cost of Laying 100 Yards of Double Conductor of Bare Copper carried

on Insulators in a Culvert._

---------------------------+----------+---------+---------+

Area in square inches      |   0·25   |  0·5    |   1·0   |

Area in square millimetres |  161·25  | 322·5   |   645   |

Weight of copper in lb.    |          |         |         |

per 100 yards           |   576    |  1153   |  2306   |

Cost of copper at          |          |         |         |

7¾_d._ per lb.          | £18 15  0| 37  5  0| 74 10  0|

Laying                     |   9  0  0|  9 12  0|  9 12  0|

Insulators                 |   0  4  6|  0  4  6|  0  4  6|

6 surface boxes and        |          |         |         |

connections              |  10  0  0| 10  0  0| 10  0  0|

Culvert, 18 inches ×       |          |         |         |

12 inches, for          |          |         |         |

two lines conductor,    |          |         |         |

in brickwork            |  53  8  0| 53  8  0| 53  8  0|

and cement, replacing   |          |         |         |

pavement                |          |         |         |

Engineers and              |          |         |         |

superintendence         |   6  0  0| 10  0  0| 10  0  0|

+----------+---------+---------+

Total                | £97  7  6|120  9  6|157 14  6|

Extra for copper at        |          |         |         |

9½_d._ per lb.          |   3  5  0|  8 10  0| 17  0  0|

+----------+---------+---------+

Total                |£100 12  6|128 19  6|174 14  6|

Cost of copper per lb.     |          |         |         |

laid complete          |  42_d._  | 27_d._  | 18·2_d._|

Current in ampères         |    90    |  180    |  360    |

Cost per ampère            |   1  2  3|  0 14  5|  0  9  8|

---------------------------+----------+---------+---------+

---------------------------+---------+---------+-------------

Area in square inches      |   2·0   |  2·55   |  3·00

Area in square millimetres |  1290   |  1645   |  1935

Weight of copper in lb.    |         |         |

per 100 yards            |  4612   |  6125   |  6918

Cost of copper at          |         |         |

7¾_d._ per lb.           |149  0  0|190  0  0|224  0  0

Laying                     |  9 15  0|  9 15  0| 10  0  0

Insulators                 |  0  4  6|  0  4  6|  0  4  6

6 surface boxes and        |         |         |

connections              | 10  0  0| 10  0  0| 10  0  0

Culvert, 18 inches ×       |         |         |

12 inches, for           |         |         |

two lines conductor,     |         |         |

in brickwork             | 53  8  0| 53  8  0| 53  8  0

and cement,              |         |         |

replacing pavement       |         |         |

Engineers and              |         |         |

superintendence          | 10  0  0| 10  0  0| 15  0  0

+---------+---------+-------------

Total                |232  7  6|263  7  6|312 12  6

Extra for copper at        |         |         |

9½_d._ per lb.           | 34  0  0| 43 10  0| 51  0  0

+---------+---------+-------------

Total                |266  7  6|306  7  6|363 12  6

Cost of copper per lb.     |         |         |

laid complete            | 13·8_d._|  12_d._ |  12 6_d._

Current in ampères         |   720   |  910    |  1080

Cost per ampère            |  0  7  5|  0  6  9|  0  6  8½

---------------------------+---------+---------+-------------

THE VIENNA CENTRAL-STATION.

The practical success of the Battery Transformer system has been

demonstrated at Vienna, where an installation of five thousand lamps

in the Opera House and Burg Theatre was maintained for the past year

from a distributing station 1,400 yards away. The boilers are fixed

in a basement formed by excavating the court-yard of a private house

to a depth of 15 feet 6 in. below the street level; the building

itself is utilised partly for offices and partly as a large dynamo and

engine-room. Each dynamo is designed to give an output of 72 kilowatts

or 120 ampères, at 600 volts pressure. The current is led by means of a

lead-covered cable underground to the accumulators, which are erected

in groups of 52 cells each, so as to give 100 volts to the lamps, with

a comfortable margin. The total pressure required to charge the four

groups of batteries in series varies from 430 volts at the time the

batteries are giving off work, to 480 volts for the short time during

which the charge is being completed. During five hours of lighting

about two-thirds of the current comes direct from the dynamos; but

during this time, for short periods, the demand for current often

increases to such an extent that these proportions may be reversed, and

the batteries supply two-thirds of the total.

The regulation of groups of batteries placed in series is not a

difficult matter, and will be understood by referring to the following

diagram, Fig. 27:—

[Illustration: FIG. 27.]

The four battery stations mentioned as arranged in series are

represented. The current may be supposed to enter at the right hand

corner, passing through the first battery with the lamps parallel to

it, and from that battery to the commencement of the next, and so on

through the third and fourth, the current being varied at will at the

central-station, or kept constant by means of an electrical governor.

The potential for each of the four groups of lamps is maintained in

the following manner:—In each group one terminal is kept permanently

connected to one of the discharge mains and to one of the charging

mains; the other terminal can be shifted from cell to cell according to

the E. M. F. required in the corresponding lamp circuit by means of a

contact regulator. This movable terminal is shown by the bunch of lines

at one extremity of each battery group. The rule for charge and

discharge is, that the terminal cell at the regulating end of the

battery is so arranged that it neither receives nor gives off current,

so that there is no loss of energy in the shape of E. M. F. The contact

regulator, which was designed by Mr. Crompton for use at Kensington

Court, is shown by Fig. 28:—

[Illustration: FIG. 28.

CENTRAL-STATION.]

The ring contacts are arranged in a line in such a manner that a

circular contact-piece, made of thin sheets of copper, can be forced

through them in turn by means of a central screw spindle. The mains for

charge and discharge are attached to the fixed disc contacts on the

central screws, and the regulating cells of the battery are coupled to

their respective contact rings by sockets at the back of the board.

The difficulty with the battery transformer system is the introduction

of 400 to 500 volts into the houses, which would be necessary

without the batteries are always fixed in sub-stations from which

a low-pressure current, say of 100 volts E. M. F., could only be

distributed.

A method has been devised by Mr. Henry Edmunds to obviate this

disadvantage. He also uses the high-tension current to charge the

batteries, but by means of a distributor, which is automatically

worked by the current, each group of cells is charged in turn, when it

is entirely cut off from the supply main to the house, through which

current is perhaps being taken for lighting purposes. The system is now

being adopted by the Cadogan Electricity Supply Company, Chelsea.

DIRECT-CURRENT TRANSFORMERS OR DYNAMOTORS.

The method of transforming by direct current without the aid of

batteries is not practically at work; but, as the advantages are so

obvious and its development is only a question of time, a description

of the system may not be considered out of place.

The electrical exhibition at Philadelphia in 1884 contained a dynamotor

which was exhibited by the Van de Poele Electric-Light Company, but,

as far as could be ascertained, was not worked, and, as it was simply

described as an induction machine for distributing currents for the use

of incandescent and other lights, it attracted little attention.

The advantages of an alternating current transformer system of

distribution, Class II., has been put forward in these pages,

especially that of simplicity and cheapness. An alternating current

dynamo for a given output is cheaper than a direct, and it takes less

labour to look after it, because it has no commutator.

An alternating transformer is also an exceedingly simple piece of

apparatus. If originally made with due care and kept in a dry place, it

never breaks down, as it has no moving parts, and so there is nothing

to go wrong.

The alternating system of distribution has, however, some very serious

disadvantages. In the first place, it is most important that motors

should be driven during the day when the lights are not in use. In the

second, batteries cannot be used in an alternating current system, so

any immunity from breakdown that they might ensure is wanting; and

steam must be kept up all day and all night.

If motors are wanted during the day, so that the load on the engine is

nearly constant, batteries are not so valuable, except with a view of

preventing a breakdown; but, if batteries cannot be used, the advantage

of using motors becomes enormous, as the plant has to be large enough

to supply the maximum load, and would otherwise be idle during the day.

In alternating current systems there are two difficulties in the way

of using motors. It is difficult to make an alternating current motor

that will start, and, if that difficulty is surmounted, it is difficult

to make an alternating current motor that will work on varying loads

without great waste of power. The question of the efficiency of

alternating current motors has never been really practically studied

yet; and, until these difficulties are overcome, we must regard

alternating current motors as non-existent. Several methods of working

alternating current transformers off direct currents by commutating the

primary have been proposed at different times; but they all seem to be

impracticable, and it seems impossible to get over the difficulties

that arise from sparking when it is attempted to break a high-tension

circuit.

One of the first methods of distribution over large areas proposed was

by means of motors and dynamos combined. For instance, suppose, in

order to keep down the size of the leads, 2,000 volts are used in the

mains, a motor capable of working with 2,000 volts is put down where

the lights are wanted, and this is made to drive a dynamo giving 100

volts and a large current. Instead of having a separate motor and a

dynamo connected by a belt or by coupling the spindles together, it is

simpler to make one machine with two armatures, or to have only one

armature with two circuits on it. One circuit is wound with fine wire

and takes the 2,000 volts and tends to turn the armature round. The

other circuit is wound with thick wire giving 100 volts and a large

current, and tends to stop the armature, thus absorbing the power

supplied by the high-pressure circuit. The direct-current transformer

or dynamotor is thus a sort of double dynamo, or dynamo and motor

combined. If it gets 2,000 volts and 10 ampères, it would, if there

were no waste, give 100 volts and 200 ampères; with a waste of 10 per

cent., it will give 100 volts and 180 ampères.

In the United States it is usual to place an alternating current motor

in each house to be lighted; but the conditions are quite different

there, overhead wires being used extensively. In this country this

system is not likely to find favour, and local sub-stations will be

used, the high pressure, which is always dangerous to life, will

thus be kept out of private houses and offices. There is, then,

very little difference in the cost of maintenance of alternating

current transformers and dynamotors, and the advantages possessed

by alternating current transformers in this respect are more than

counter-balanced by the use of motors on direct current circuits.

Dynamotors have not come into general use yet because no stations have

been started in this country of the size which demands them. No central

station with sub-stations is in operation, but there is every reason to

expect several will be soon; and it is very necessary to discuss the

various methods, not only in use at this moment but coming into use in

the immediate future. The dynamotor itself needs no working out, as

any maker of direct-current dynamos can, of course, make them. Messrs.

Paris and Scott of Norwich showed some in operation at the Newcastle

Exhibition in 1887; the most successful type is that recently invented

by Mr. Jas. Swinburne, illustrated by Fig. 29. The backward main round

primary or motor magnet is shown on the left, and the forward main

round the secondary or dynamo magnet on the right, the outside coil

round both magnets is the shunt.

[Illustration: FIG. 29.]

The dynamotor may be made with two circuits on one armature as

already explained, or it may have two armatures in separate fields,

still making up one machine. The first arrangement has two grave

disadvantages. There is difficulty about securing perfect insulation

between the two circuits, and this leads to chances of danger in the

houses. A dynamotor with two circuits on one armature cannot be

compounded, that is to say, it cannot be made to give constant

electrical pressure on the mains if the number of lamps is varied. A

Swinburne double armature machine can be compounded, not only to give

constant pressure with a varying load, but to give constant electrical

pressure even if both the load and the pressure on the primary circuit

vary. This makes a considerable difference in the copper of the primary

leads, as in large and complicated districts it is almost impossible

to arrange leads, even when working with high electrical pressure and

small currents, so that the electrical pressure remains constant,

or even nearly so. A very small variation of the pressure on an

incandescent lamp makes an enormous difference in the amount of light

it gives, and in its duration. It is, therefore, most important that

the E. M. F. on the lamps should be kept absolutely constant.

This difficulty is, of course, insurmountable in the case of

alternating current transformers. Alternating current transformers

cannot be made to compound, and the loss in leads cannot be corrected

by them, so that the lamps burn dull at full load.

If secondary batteries are used at the sub-stations, the reduction of

pressure might be effected by them. A number would be charged in series

and discharged in parallel. This arrangement needs at least two sets

of cells, and cells are expensive; and it is difficult to preserve the

insulation of cells with such electrical pressure as 2,000 volts. If

cells are used for the purpose of equalising the load or as a safety

reserve, it is better to charge them by means of a dynamotor.

INSTALLATION AND WORKING COST OF CENTRAL-STATIONS.

Until the balance-sheet of some large central-station has been

published, it is impossible to do more than surmise what relation the

earning power of the generating plant bears to the initial cost. Those

central-stations which are working successfully in this country at the

present time are either too small for a reliable estimate to be formed,

or, as in the case of the Grosvenor Gallery, the space is too cramped

for the large amount of machinery which it has been found necessary

to add in order to meet the increasing demands for light. In order to

obtain an approximate idea of the cost of installing a station capable

of maintaining 10,000 lights, the following data (Table III.) given

in Mr. Crompton’s paper before the Society of Telegraph Engineers are

extremely valuable and will be examined with interest.

Although the figures given are necessarily empirical and open to

criticism, the cost with both systems of distribution is approximately

the same, and may be taken roughly at £5,860 per 1,000 lights, which

amount, according to Professor Forbes, would be reduced to £3,914 per

1,000 lights if the installation was put down according to American

practice, and at the initial cost of the Westinghouse alternating

current system.

Mr. Crompton also compares the working cost of the two systems (Table

IV.).

TABLE III.

_Cost of 10,000-Light, or 600-Kilowatt_,[6] _Plant._

A.T.—ALTERNATING TRANSFORMER DISTRIBUTION.

Generating station, buildings, chimney shaft,                £

water tanks, and general fittings                        11,000

Dynamos and exciters—865 kilowatts, including

spare sets, divided as convenient                         5,540

Motive power, _i.e._, engines, boilers, steam

and feed connections, belts, &c., at £8 12_s._

per I.H.P.                                               12,470

500 transformers, _i.e._, one to every pair of

houses, at £15 each                                       7,500

2,000 yards primary or charging main, exterior

to area of supply, at £308 per 100 yards                  6,160

20,000 yards distributing main, 50 mm. sectional

area, at £91 7_s._ (_see_ Table I.)                      14,270

Regulating gear                                               500

———————

£57,440

=======

B.T.—ACCUMULATOR TRANSFORMER DISTRIBUTION.

Generating station, buildings, chimney stack,                £

water tanks, and general fittings                         8,000

Dynamos—600 kilowatts, in six sets of 100

kilowatts each                                            4,800

Motive power, _i.e._, engines, boilers, steam

and feed connections, &c., at £8 12_s._

per I.H.P.                                                8,600

4 groups of accumulators, in all 240 cells, in

series, at £40 per cell, including stands                 9,600

2,000 yards charging main, at £306 17_s._ 6_d._

per 100 yards (_see_ Table II.)                           6,137

20,000 yards distributing main, 161·25 mm. sectional

area, at £100 12_s._ 6_d._ (_see_ Table II.)             20,125

Regulating gear                                             2,500

———————

£59,762

=======

[6] Kilowatt equals 1,000 watts.

TABLE IV.

_Working Expenses and Maintenance of 10,000-Light,

or 600-Kilowatt, Plant._

-------------------------------+-----------------------------------+

|        Direct Alternating         |

|        Transformer System.        |

-------------------------------+-----------------+-----------------+

_Materials_—                   |   £   _s._ _d._ |   £   _s._ _d._ |

Coals: 4,380 tons at 17_s._   | 3,723  0    0   |                 |

”    2,550   ”     17_s._   |       · ·       |                 |

Oil, water, and petty stores: |                 |                 |

1,500 hours at 7_s._ 6_d._ |                 |                 |

7,250 hours at 1_s._       |   925  0    0   |                 |

1,400 hours at 5_s._       |       · ·       |                 |

Total cost of material   +-----------------+ 4,648  0    0   |

|                 |                 |

_Labour_—                      |                 |                 |

2 foreman drivers at 45_s._; |                 |                 |

6 drivers at 30_s._;         |                 |                 |

9 firemen at 24_s._;         |                 |                 |

sundry labour             | 1,388  8     0  |                 |

|                 |                 |

1 foreman driver at 45_s._;  |                 |                 |

2 drivers at 30_s._;         |                 |                 |

3 firemen at 24_s._;         |                 |                 |

sundry labour             |                 |                 |

|                 |                 |

_Salaries_—                    |                 |                 |

1 chief at £500;            |                 |                 |

2 assistants at £200 each;  |                 |                 |

4 clerks at £80 each        | 1,220  0     0  |                 |

|                 |                 |

1 chief at £500;            |                 |                 |

1 assistant at £200;        |                 |                 |

4 clerks at £80 each        |       · ·       |                 |

+-----------------+ 2,608  8    0   |

_Maintenance of Plant_—        |                 |                 |

Motive power and dynamos:    |                 |                 |

10 per cent. on £18,010    | 1,801  0     0  |                 |

10 per cent. on £13,400    |       · ·       |                 |

Buildings and fittings:      |                 |                 |

5 per cent. on £11,000    |   550  0     0  |                 |

5 per cent. on £8,000     |       · ·       |                 |

Transformers:                |                 |                 |

10 per cent. on £7,500     |   750  0     0  |                 |

Accumulators:                |                 |                 |

15 per cent. on £9,600     |       · ·       |                 |

Mains:                       |                 |                 |

7½ per cent. on £20,430   | 1,532  5     0  |                 |

2½ per cent. on £26,262   |       · ·       |                 |

Regulating gear:             |                 |                 |

10 per cent. on £500       |    50  0     0  |                 |

10 per cent. on £2,500     |       · ·       |                 |

+-----------------+ 4,683  5    0   |

|                 +-----------------+

|                 |11,939 13    0   |

|                 +-----------------+

2,100 units × 365 days       |                 |                 |

= 766,500 units.       |                 |                 |

Cost per unit       |       · ·       |    3·75_d._     |

====================================================================

|         Continuous Battery        |

|         Transformer System.       |

-------------------------------+-----------------+-----------------+

_Materials_—                   |   £   _s._ _d._ |   £   _s._ _d._ |

Coals: 4,380 tons at 17_s._   |       · ·       |                 |

”    2,550   ”     17_s._   | 2,167  0    0   |                 |

Oil, water, and petty stores: |                 |                 |

1,500 hours at 7_s._ 6_d._ |                 |                 |

7,250 hours at 1_s._       |       · ·       |                 |

1,400 hours at 5_s._       |   350  0    0   |                 |

Total cost of material   +-----------------+ 2,517  0    0   |

|                 |                 |

_Labour_—                      |                 |                 |

2 foreman drivers at 45_s._; |                 |                 |

6 drivers at 30_s._;         |                 |                 |

9 firemen at 24_s._;         |                 |                 |

sundry labour             |                 |                 |

|                 |                 |

1 foreman driver at 45_s._;  |                 |                 |

2 drivers at 30_s._;         |                 |                 |

3 firemen at 24_s._;         |                 |                 |

sundry labour             |  975  0    0    |                 |

|                 |                 |

_Salaries_—                    |                 |                 |

1 chief at £500;            |                 |                 |

2 assistants at £200 each;  |                 |                 |

4 clerks at £80 each        |       · ·       |                 |

|                 |                 |

1 chief at £500;            |                 |                 |

1 assistant at £200;        |                 |                 |

4 clerks at £80 each        | 1,020  0    0   |                 |

+-----------------+ 1,995  0    0   |

_Maintenance of Plant_—        |                 |                 |

Motive power and dynamos:    |                 |                 |

10 per cent. on £18,010    |       · ·       |                 |

10 per cent. on £13,400    | 1,340  0    0   |                 |

Buildings and fittings:      |                 |                 |

5 per cent. on £11,000    |       · ·       |                 |

5 per cent. on £8,000     |   400  0    0   |                 |

Transformers:                |                 |                 |

10 per cent. on £7,500     |       · ·       |                 |

Accumulators:                |                 |                 |

15 per cent. on £9,600     | 1,440  0    0   |                 |

Mains:                       |                 |                 |

7½ per cent. on £20,430   |       · ·       |                 |

2½ per cent. on £26,262   |   656 10    0   |                 |

Regulating gear:             |                 |                 |

10 per cent. on £500       |       · ·       |                 |

10 per cent. on £2,500     |   250  0    0   |                 |

+-----------------+ 4,086 10    0   |

+                 +-----------------+

|                 | 8,598 10    0   |

+                 +-----------------+

2,100 units × 365 days       |                 |                 |

= 766,500 units.       |                 |                 |

Cost per unit       |       · ·       |     2·7_d._     |

-------------------------------+-----------------+-----------------+

With the exception of the amount allowed for depreciation of the

accumulators, which time alone can show to be correct, the expenses

may be said to be over rather than under-estimated; the 15 per cent.

depreciation given in Table IV. is under what has hitherto been found

necessary to allow for the renewal of the plates of a secondary battery.

If the mean of the two results in Table IV. are taken, the working cost

per Board of Trade Unit will be 3·22_d._, which shows that with both

systems, after making due allowance for interest on capital, directors’

fees, bad debts, and other sundries omitted by Mr. Crompton, there is a

probability of a very fair return on the capital expenditure, and the

prospect of a handsome dividend for an electric lighting company who

can sell electricity at the average price of 7_d._ per Unit.

*       *       *       *       *

The cost of maintaining and working electric lighting plant at

private installations is usually much in excess of a supply from a

central-station; but where the installation is over 500 lights, the

difference is not very great.

The working cost at the Athenæum Club of 387 lamps for the past year is

given as follows:—

£    _s.   d._

Gas for gas-engine          446    7    10

Oil     ”     ”              71    3     8

Water   ”     ”              35    0     0

Wages                       175    2     1

Sundries                     30    3     0

Maintenance of lamps, etc.   98    4     1

Repairs                     103    1     1

—————

£959    1     9

—————

Average cost of lighting by gas and oil for previous years, for

two-thirds number of lights £840.

At the Naval and Military Club, 420 lights cost £821 18_s._ for the

same period, a steam-engine being used instead of a gas-engine.

The annual report of the cost of the electric light at the South

Kensington Museum shows that in a larger installation, consisting both

of arc and incandescent lamps, the annual cost of the latter is much

less than in either of the clubs mentioned. At the Museum there are 860

16 candle-power lamps, working 655½ hours per annum, or 562,387 lamp

hours; the total cost for working last year was £386, which includes

£66 for repairs of engines, boilers, dynamos, and maintenance of lamps;

but rent, interest on capital, depreciation of plant, and management

is not included. The light is used only three evenings a week, so that

the wages of the attendants are proportionately in excess of what they

would be in a central-station.

*       *       *       *       *

The cost of arc lighting for street purposes may be estimated from the

following tenders. At Taunton the local electric light company offered

to extend the lighting of streets from 29 to 60 arc lamps of 1,200

candle-power nominal on the Thomson-Houston system, at the following

rate:—

Per annum.

£ _s.   d._

Burning on average of 6 hours per night each lamp  17   7   6

7       ”            ”       18  12   6

8       ”            ”       19  17   6

The posts and supports to be provided and fixed by the company, or, if

the town council found the same, the company would allow a deduction at

the rate of 5 per cent. per annum upon the outlay made by the council.

The lamps are usually about 400 feet apart.

The actual cost of operating arc lights on this system is given in the

following detailed expenses of a six hours’ run of a 50-light plant for

the street lighting of an American city:—

2,600 lb. Ind. nut and slack coal, at $1·30 per ton     $1·69

Engineer, one night, at $50·00 per month                 1·67

Superintendent or electrician, one night, at $50·00

per month                                             1·67

Trimmer, one day, at $40·00 per month                    1·33

48 pairs of carbons, at $18·50 per month                   89

Waste, &c., at $20·00 per year                             05

Water rent, at $40·00 per year                             11

Half-pint cylinder oil, at 60c. per gallon                 04

One pint engine and dynamo oil, at 50c. per gallon         06

One day repairs on machine and lamps, including

globes, at $120·00 per year                             33

One day taxes on 50-light plant, assessed at $5,000,

at 2¼ per cent.                                         31

One day interest on 50-light plant ($10,000), at 6 per

cent.                                                 1·67

—————

Making a total of                                      $9·82

10½_d._ or 20·45 cents. per lamp. £15 10_s._ per annum.

If, in addition to the 50 street lights, 33 other arc lights are

maintained, the total cost is reduced for a six hours’ run to $13·25,

or £2 15_s._ 2_d._ for the 83 lights, 8_d._ or 15·96 cents per lamp,

£12 3_s._ 4_d._ per annum.

Table V. has been calculated by M. Decker, of Nuremburg, and gives

the comparative cost of working 150 lamps by electricity and by gas.

The gas price (1) is that paid in Paris, namely, 6_s._ 9_d._ per 1000

cubic feet; column (2) is the price usually taken commercially, which

includes the fixed charges. The price of electricity is given: 1st,

when a steam-engine is available; 2nd, when it is necessary to lay down

a special engine; 3rd, when a gas-engine is used the gas is charged at

a trifle over the price in column (1).

TABLE V.

_Total Cost per Hour and per Lamp._

Legend for Table V.

A = Number of hours’ work per year.

B = Number of hours’ work per day.

C = Steam-engine (existing).

D = Hydraulic Motor.

E = Steam-engine to be erected.

F = Gas engine

G = (1) Gas at 6_s._ 9_d._ per 1,000 ft.

H = (2) Gas at 8_s._ 9_d._ per 1,000 ft.

--------+------+--------+--------+---------+---------+-------+------

|      |        |        |         |         |       |

A  |  B   |   C    |   D    |   E     |    F    |   G   |   H

|      |        |        |         |         |       |

--------+------+--------+--------+---------+---------+-------+------

|      | Pence. | Pence. |  Pence. |  Pence. | Pence.| Pence.

500  | 1·38 | 0·485  |        |  1·055  |  1·216  | 0·418 | 0·552

800  | 2·19 | 0·371  |        |  0·780  |  1·007  | 0·399 | 0·513

1,200  | 3·29 | 0·314  |        |  0·608  |  0·865  | 0·380 | 0·352

3,600  | 9·87 | 0·219  | 0·152  |  0·352  |  0·485  | 0·361 | 0·465

Arc Lamps.

500  | 1·38 | 5·235  | 4·246  | 10·459  | 11·485  |       |

800  | 2·19 | 3·971  | 3·089  |  7·552  |  9·272  |       |

1,200  | 3·29 | 3·087  | 2·441  |  6·004  |  7·581  |       |

3,600  | 9·87 | 2·185  | 1·510  |  3·591  |  5·586  |       |

--------+------+--------+--------+---------+---------+-------+------

UNDERGROUND OR OVERHEAD WIRES.

Apart from the unsightly appearance of overhead wires, there are many

reasons why any extended system of supply of electricity should be

carried out by underground cables. It is true that there have been no

accidents in this country due to electric light wires falling, owing to

the care bestowed on their insulation and erection; on account of the

heat generated by the passage of the current through the leads no snow

can accumulate on them, and therefore they are not subjected to the

extra weight which destroyed so many of the telegraph and telephone

wires in the last snow storm. Overhead electric light wires are

exclusively used by the largest electric-supply company in London, and

it is probable that, without further legislation takes place, other

companies will shirk the expense of an underground system; and even

a more dangerous method of running cables than that which has been

condemned in the principal cities of the United States will become

not the exception but the rule. In the city of New York the process

of conversion of the present overhead to an underground system is a

fact about to be accomplished to a very great extent at least, in the

near future. Since July, 1887, the Western Union Telegraph Company

have occupied the conduits, which have been constructed and laid with

some 500 miles of wire; also the Metropolitan Telephone and Telegraph

Company have 1000 miles of wire in the subways; and the Edison

Illuminating Company, whose conductors were laid in the trench at the

time of construction, has more than 1000 miles of underground cable.

The plan adopted is to build conduits of section, as in Fig. 30, which

shows the subway in course of construction, with man-hole opening and

exposed ends of conduits. The single tube at top is for distribution

between man-holes, and some wires are shown entering the vault on the

right from the service box in the foreground. The conduits are of

various types; creosoted wooden tubes are placed in creosoted wooden

casings; wrought-iron pipes are sometimes laid in asphaltic concrete

with creosoted wooden box; another arrangement is to be of composition

blocks on concrete, and cover them with brick—or wrought-iron pipe

is lined with cement, and laid in hydraulic cement concrete and cased

with creosoted plank. About 85 per cent. of all the conduits have been

constructed on this plan, the interior diameter of the pipes being 2½

inches.

[Illustration: FIG. 30.]

[Illustration: FIG. 31.]

Fig. 31 shows how the street arc lighting wires are taken, also a

branch for house use, out of the man-holes, which are placed at each

street crossing. For the cleaning purposes and for drawing the cable

through the conduits, these must be laid practically straight.

[Illustration: FIG. 32.]

Fig. 32 illustrates a method proposed by Mr. Kenneth Mackenzie, which

is somewhat similar to the system of conduit which, used at Tours

for the past two years, has been found most efficient for the high

potential supply mains to the transformers. The troughs would be about

4 ft. long and 15 in. deep, having spigot and socket joints at the ends

like ordinary water pipes. Transverse pieces of wood, or preferably

slate, would rest upon projections, and would support the mains, and

a cover recessed as shown would make the conduit fairly water-tight;

drain holes would be provided, and the branches to houses led off

through glands in the side of troughs. The American plan is, doubtless,

the best, as there is no space for moisture to collect in the conduits;

but Mr. Mackenzie’s system is well worth trying, and has the advantage

of being much cheaper in first cost.

The Edison plan is to place two solid conductors in a tube which is

filled up solid with an insulating material, suitable bends and offsets

being supplied, so that the tube containing the two conductors can be

buried in the ground like a gas-pipe. The system is very largely used

both in the United States and in Continental cities; but it is doubtful

whether the protection would suffice in our towns, where the streets

are already at the mercy of the gas and water companies, whose workmen,

with a single blow of a pick, might perforate the tube, and cause a

dangerous short circuit.

THE INTERESTS OF GAS COMPANIES AS TO ELECTRIC LIGHTING.

The policy of gas companies with regard to electric light has, with

few exceptions, been a state of indifference to the progress of

things electric, with contempt for a rival whose opposition is not

sufficiently powerful to be appreciated. The chairman of a well-known

gas company stated, what is undisputed,—that the introduction of

electric arc lights was accompanied by an increased consumption of gas

in the immediate neighbourhood where these lights are used; but it is

very doubtful whether this will be the case when incandescent lights

are generally supplied. The introduction of these lights into any

business district would mean the displacement of at least as many

burners as there are electric lamps; and this reduction not only

means loss of income, but also loss by interest on plant which is not

kept at work to the capacity for which it was designed. The question

suggests itself, “Are existing gas companies more favourably situated

for furnishing electricity than any one else?” There are many reasons

in favour of the supposition that the directors of gas companies have

at the present time an opportunity of acquiring almost as complete a

monopoly of lighting by electricity as they have with gas. As regards

central-stations, everything is in their favour; there is generally

some spare ground for the machinery, waste heat could be utilised, and

a cheap fuel in the shape of coke is ready to hand. They have greater

facilities for breaking up streets without danger of troubles arising

with the local authorities, and if the Gasworks Clauses Acts, which

authorise their existence, tie them down to one illuminant, a very

little expenditure would enable them to enlarge their powers. In many

towns the shareholders are local men who wish to use the electric

light, but cannot favour its introduction because they think it would

tend to smaller dividends or lower quotations for their shares; if,

however, a scheme was promoted either by the gas company, or, if that

was impossible, if the directors interested themselves in a separate

electric light undertaking, the security which the gas and water

investments command would, no doubt, cause a sufficient number of local

subscribers to come forward and make even a small installation a paying

concern. The Imperial Continental Gas Association have already taken

up the supply of electricity in Vienna, and are likely to extend this

new branch of their business to the other cities in which they hold

gas concessions; also in the United States the growing opposition of

the electric light companies is being seriously discussed, and already

several gas companies are installing electric light plants.

It is not at all probable that the scare which caused such a drop

in the value of gas shares when the electric light first appeared

will be repeated, but the present high price of gas shares cannot

be maintained. Kerosene lamps have been for some time a far greater

rival to gas than electricity. The cheapening of petroleum, which is

now shipped in bulk to this country in tank steamers, will cause the

consumption to increase, and enable the oil to be supplied at a price

so that it can be used in petroleum-engines, and give a motive power

which will be found to be far more economical than the gas-engine.

The latest development of petroleum-engines is that shown by Messrs.

Priestman at the Royal Agricultural Society’s Show at Nottingham. The

engine in external appearance is like the Otto gas-engine, but uses the

ordinary “paraffin oil” of commerce, which has a high flashing point.

The oil is simply put into a closed tank, and on the top of this, air

is forced which drives the petroleum into a chamber heated by the

exhaust from the engine, where it is partially vaporised and led into

the cylinder with sufficient air to cause it to ignite by means of an

electric spark.

The report of the trials with a 5 horse-power engine show that a brake

horse-power was obtained for 1·7 lb. of oil, or at 6½_d._ per gallon

for 1·4_d._ per horse-power per hour; with the Spiel engine the cost is

stated to be 0·8_d._ per horse-power per hour.

Any serious reverse to the gas industry would cause a great pecuniary

loss to a large number of investors. The paid-up and borrowed capital

devoted to the manufacture and supply of gas in the United Kingdom

exceeds £56,000,000, of which above £36,000,000 appertain to the

companies and the remainder to the local authorities, whose receipts in

respect of their gas undertakings last year exceeded £4,400,000.

The corporation of Bradford, who are owners of the gasworks, have

wisely foreseen that it is better to keep the electric light in their

own hands, and are now about to erect a central-station, and will

lay underground wires; the amount sanctioned for this preliminary

installation is £20,000.

THE LUCIGEN LIGHT.

A few remarks on this method of obtaining light from the combustion

of crude petroleum may be added, as the light has been put forward

as a cheaper and better substitute for the electric arc. The Lucigen

light is produced by burning creosote oil, tar oil, or other heavy

hydro-carbons, by means of compressed air in a special form of lamp,

and consists of a cylinder at the side of which a steam donkey

compressing pump is mounted, or in a more recent form known as the

Wells’ light, no separate air compressor is used, but, instead, the

pressure is obtained from the water mains or from a small force pump.

The cost is stated to be 3_d._ per hour for 2,500 candle-power,

requiring three gallons of oil per hour, but is in reality at the

present time double this owing to the price of the oil, which, under

the most advantageous circumstances, costs on average 2_d._ per

gallon. At the Forth Bridge these lights have been found of use in

illuminating open spaces, but have not supplanted the electric arc

lights which are universally employed for the lighting of the works and

the interior of the shops. The disadvantages are the noise, the oil

shower which pervades the vicinity of the light causing timber staging

to be highly inflammable, and the difficulty of preventing water from

entering the burner, a few drops sufficing to extinguish the light.

The use of the Lucigen light is, therefore, very limited, and it is

probable that, in situations where shadows from the arc light are found

to be objectionable, large incandescent electric lamps, which are

supplied up to 1,500 candle-power, would meet the case; or, failing

these, petroleum could be burnt in lamps similar to those used in

lighthouses with greater safety, and at not much increased cost, than

the compressed-air system.

USEFUL NOTES.

To ascertain in what direction the electric current is flowing through

any wire by means of a pocket compass:—

A current flowing from _south_ to _north_ will always deflect the

needle to the west, providing the wire in which the current flows is

_over_ the instrument.

The word S. N. O. W. expresses this—south north over west; and should

be remembered.

_Another simple plan_ is to hold the outstretched right hand over the

compass; then, if the current flows in the direction of the wrist to

the fingers, the needle will move towards the thumb.

To find the direction of the current in the wire of an electro-magnet:

Place the palm of the hand on the coil with the fingers parallel to

the wires: the thumb will point to the _North Pole_ if the current is

flowing as in previous rule towards the fingers. Conversely: if the

_North Pole_ is known, the fingers will point to the direction of the

current when placed parallel with the wires, with the thumb pointing to

the North Pole.

If no compass is available, take two pieces of lead and place a few

inches apart in a pot containing dilute sulphuric acid, scrape the lead

clean, and join a piece of wire to each and connect to poles to be

tested. After current has passed a short time one piece of lead will

become brown, the other grey; trace the former to the dynamo cable, and

this is the positive, and should be marked with a + or be painted red

for future distinction.

_Incandescent Lights or Glow Lights._

The number of lights required to illuminate any room would vary very

much, according to the style of decoration and position of the lamps.

As a rule, a similar number of glow lamps are required as there would

be gas burners. The former give a much higher standard of illumination,

which, curiously enough, is generally expected with electric lighting

on account of the purity of the atmosphere when the full light is being

used, which is not the case with gas.

One 16 candle-power lamp will light an area of about 8 feet in diameter

at 8 feet above ground; in ordinary situations allow, one lamp for 38

square feet.

_Arc Lighting of Works._

External.—56. 2,000 CP. arc lights will illuminate 160,000 square

yards, or one for each 2,800 square yards.

Internal.—43. 2,000 CP. arc lights will illuminate 31,500 square

yards, or one for each 730 square yards.

_Approximate Cost of Electric Light, Museum._

Arc lighting, 2/5 gas; with interest, ⅔.

Incandescent,   ⅔ gas; with interest, 4/3.

_Motive Power._

Compound engine 2 lbs. of coal per indicated horse-power per hour.

Good single-acting engine 3 to 6 per indicated horse-power per hour.

An indicated horse-power can be obtained in a compound engine from 20

lbs. of steam per hour.

A good boiler evaporates 9 to 10 lbs. of water per lb. of coal.

From 21 to 28 cubic feet of gas are required in a gas-engine per

indicated horse-power per hour.

_Incandescent Lamps._

In practice allow 9-60 watt 16 CP. lamps per indicated horse-power of

engine.

_Mem. for Wire Running._

Leads to the left or “low,” “_light coloured_.”

Returns to the right or “raised,” “_red_.”

_English and French Measures._

Millimetre   =  0·039 inches   1 mill =  ·0254  millimetres.

Centimetre   =  0·393   ”      1 inch = 2·5399  centimetres.

Decimetre    =  3·93    ”      1 foot = 3·3480  decimetres.

Metre        = 39·37    ”      1 yard =  ·91439 metres.

Cubic metre  = 35·32 cubic feet or 1·31 cubic yards.

ELECTRICAL MEASUREMENTS.

The Paris Congress Units (1884) are now universally adopted and consist

as follows:

_Electro-motive Force, and Potential_ (E).—The Volt. _The legal volt

is ·926 of the E. M. F. of a Daniell’s cell, which for rough purposes

may be taken as a volt._

_Resistance_ (R).—The Ohm. The legal ohm is now represented by the

resistance of a column of mercury of a square millimetre in section at

the temperature of zero centigrade 1·062 metres long.

_Current_ (C).—The Ampère. This is the strength of current sent

through a wire having the resistance of 1 ohm at the E. M. F. of 1 volt.

_Quantity_ (Q).—The Coulomb. It is the quantity of electricity given

by an ampère in a second. One coulomb decomposes ·00142 grain of water.

_Heat or Work_ (W).—The Joule, or Volt-Coulomb, is the work done by 1

coulomb in 1 ohm. The work done by any current per second is obtained

in ergs by the product of the current into the electro-motive force

producing it or W = CE or W = C²R. The Erg is the C. G. S. unit of

work.

_Power_ (P).—The Watt, 1 ÷ 746 of a horse-power, employed in doing 1

joule of work in 1 second.

HP, or the Horse-power, is found by dividing C E by 746, thus (CE)/746

or (C²R)/746 = HP.

See also explanation of terms.

ELECTRICAL TABLE OF THE BIRMINGHAM WIRE GAUGE FOR PURE COPPER.

+---+-----+-----+-------+-------+---------+--------+--------+--------+

|B. |Diam.|Diam.|Area in|Circum.| Pounds  | Feet   |  Feet  | Ohms   |

|W. | in  | in  |Square |  in   |  per    |  per   |  per   |  per   |

|G. | In. | mm. |Inches.|Inches.|  Mile.  | Pound. |  Ohm.  | 1000   |

|No.|     |     |       |       |         |        |        | Feet.  |

+---+-----+-----+-------+-------+---------+--------+--------+--------+

| 1 |·3   |7·62 |·070686|·94248 |1444·0087|  3·662 |8706·843|  ·1148 |

| 2 |·284 |7·21 |·063347|·89221 |1291·8699|  4·0988|7803·51 |  ·1282 |

| 3 |·259 |6·58 |·052685|·81367 |1074·5697|  4·9262|6490·09 |  ·1540 |

| 4 |·238 |6·04 |·044488|·74770 | 907·3683|  5·850 |5580·01 |  ·17007|

| 5 |·22  |5·59 |·038013|·69115 | 773·045 |  6·83  |4681·1  |  ·2136 |

| 6 |·203 |5·16 |·032365|·63774 | 657·205 |  8·02  |3985·7  |  ·2509 |

| 7 |·180 |4·57 |·025447|·56549 | 517·493 | 10·20  |3134·8  |  ·3190 |

| 8 |·165 |4·19 |·021382|·51836 | 434·861 | 12·14  |2633·7  |  ·3797 |

| 9 |·148 |3·76 |·017203|·46495 | 349·853 | 15·10  |2119·9  |  ·4719 |

|10 |·134 |3·40 |·014103|·42097 | 286·651 | 18·44  |1737·0  |  ·5757 |

|11 |·120 |3·05 |·011309|·37699 | 229·997 | 22·95  |1392·9  |  ·7179 |

|12 |·109 |2·77 |·009331|·34243 | 189·763 | 27·82  |1149·4  |  ·8700 |

|13 |·095 |2·41 |·007088|·29845 | 144·144 | 36·63  | 873·1  | 1·1454 |

|14 |·083 |2·11 |·005411|·26075 | 110·035 | 47·98  | 665·3  | 1·503  |

|15 |·072 |1·83 |·004071|·22619 |  82·790 | 63·77  | 501·5  | 1·9941 |

|16 |·065 |1·65 |·003318|·20420 |  67·478 | 78·25  | 408·7  | 2·4466 |

|17 |·058 |1·47 |·002642|·18221 |  51·3163|102·89  | 310·8  | 3·2176 |

|18 |·049 |1·24 |·001886|·15394 |  38·3486|137·68  | 232·3  | 4·3052 |

|19 |·042 |1·07 |·001385|·13195 |  28·1741|187·40  | 170·6  | 5·8599 |

|20 |·035 | ·89 |·000962|·10995 |  19·5677|269·83  | 118·5  | 8·4381 |

|21 |·032 | ·81 |·000804|·10053 |  16·3574|322·79  |  99·1  |10·094  |

|22 |·028 | ·71 |·000616|·08796 |  12·5242|421·58  |  75·8  |13·185  |

|23 |·025 | ·63 |·000491|·07854 |   9·9845|528·82  |  60·5  |16·539  |

|24 |·022 | ·55 |·000380|·06911 |   7·7299|683·06  |  46·8  |21·357  |

+---+-----+-----+-------+-------+---------+--------+--------+--------+

ELECTRICAL RESISTANCE OF COPPER WIRE IN FRENCH MEASUREMENTS.

+-------+------------+------+-------------+------------+----------+

| B.W.G.|  Diameter  | Area |Circumference|  Metres    |   Kg.    |

|  No.  |     in     |  in  |     in      |     per    |   per    |

|       |Millimeters.|  mm. | Millimeters.| Kilogramme.|  Metre.  |

+-------+------------+------+-------------+------------+----------+

|   1   |   7.62     | 45.6 |    23.9     |    1ᵐ.95   | 0ᵏ.514   |

|   2   |   7.21     | 40.8 |    22.6     |     2.78   |  0.360   |

|   3   |   6.58     | 34   |    20.7     |     3.33   |  0.300   |

|   4   |   6.04     | 28.7 |    19       |      3.95  |  0.253   |

|   5   |   5.59     | 24.5 |    17.6     |      4.61  |  0.217   |

|   6   |   5.16     | 21   |    16.2     |      5.43  |  0.184   |

|   7   |   4.57     | 16.4 |    14.3     |      6.90  |  0.145   |

|   8   |   4.19     | 13.8 |    13.1     |      8.20  |  0.122   |

|   9   |   3.76     | 11.1 |    11.8     |     10.20  |  0.098   |

|  10   |   3.40     |  9.1 |    10.7     |     12.50  |  0.080   |

|  11   |   3.05     |  7.3 |     9.6     |     13.50  |  0.074   |

|  12   |   2.77     |  6   |     8.7     |     18.87  |  0.053   |

|  13   |   2.41     |  4.6 |     7.6     |     24.80  |  0.0403  |

|  14   |   2.11     |  3.5 |     6.63    |     32.40  |  0.0309  |

|  15   |   1.83     |  2.63|     5.75    |     45.10  |  0.0232  |

|  16   |   1.65     |  2.14|     5.18    |     52.90  |  0.0189  |

|  17   |   1.47     |  1.70|     4.62    |     69.40  |  0.0144  |

|  18   |   1.24     |  1.21|     3.90    |     94.30  |  0.0106  |

|  19   |   1.07     |  0.9 |     3.36    |    135.10  |  0.0074  |

|  20   |   0.89     |  0.62|     2.80    |    181.8   |  0.0055  |

|  21   |   0.81     |  0.51|     2.54    |    212.8   |  0.0047  |

|  22   |   0.71     |  0.39|     2.23    |    285.7   |  0.0035  |

|  23   |   0.63     |  0.31|     1.98    |    364     |  0.0028  |

|  24   |   0.55     |  0.24|     1.73    |    465     |  0.00215 |

+-------+------------+------+-------------+------------+----------+

+-------+------------------------------+------------+--------+

| B.W.G.|        Resistance in Ohms    | Kilogrammes| Metres |

|  No.  +-----------------+------------+     per    |  per   |

|       | per Kilogramme. | per Metre. |     Ohm.   |  Ohm.  |

+-------+-----------------+------------+------------+--------+

|   1   |    0.00073515   |  0.000377  |   1360     | 2652   |

|   2   |    0.00116760   |  0.000420  |    860     | 2379   |

|   3   |    0.00168165   |  0.000505  |    595     | 1980   |

|   4   |    0.00232260   |  0.000588  |    430     | 1700   |

|   5   |    0.00322700   |  0.000700  |    310     | 1430   |

|   6   |    0.00452319   |  0.000833  |    220     | 1200   |

|   7   |    0.00731400   |  0.00106   |    137     |  945   |

|   8   |    0.01025000   |  0.00125   |     98     |  802   |

|   9   |    0.01581000   |  0.00155   |     63     |  646   |

|  10   |    0.0237500    |  0.00190   |     42.20  |  527   |

|  11   |    0.0318600    |  0.00236   |     31.40  |  424   |

|  12   |    0.0539682    |  0.00286   |     18.60  |  350   |

|  13   |    0.0932480    |  0.00376   |     10.70  |  266   |

|  14   |    0.160380     |  0.00495   |      6.26  |  202   |

|  15   |    0.294954     |  0.00654   |      3.40  |  153   |

|  16   |    0.430077     |  0.00813   |      2.30  |  123   |

|  17   |    0.73564      |  0.0106    |      1.35  |   94.5 |

|  18   |    1.33906      |  0.0142    |      0.75  |   70.4 |

|  19   |    2.60743      |  0.0193    |      0.38  |   51.9 |

|  20   |    5.05404      |  0.0278    |      0.20  |   36   |

|  21   |    7.04368      |  0.0331    |      0.14  |   30.2 |

|  22   |   12.37081      |  0.0433    |      0.08  |   23.1 |

|  23   |   19.6924       |  0.0541    |      0.05  |   18.5 |

|  24   |   32.5500       |  0.0700    |      0.03  |   14.3 |

+-------+-----------------+------------+------------+--------+

For Table of English Measurements see page 105.

EXPLANATION OF TERMS.

_Accumulator._—Another name for secondary batteries.

_Alternate Current Dynamo._—Produces currents which are

alternately positive and negative.

_Amalgamation._—Zinc is protected from local action by

having its surface coated with mercury.

_Ampère._—The Unit of current. A volt divided by an ohm.

(See Electrical Measurements, page 104.)

_Ampère Meter._—An instrument used for measuring strength

of current.

_Anode._—The positive electrode or pole of a decomposing

cell, the wire or plate connected to the copper or other

negative element of a battery. In electro-plating, it is

usually the soluble pole of the metal to be deposited.

(_v._ Cathode.)

_Arc._—The air space in which the electric light forms.

_Armature._—The keeper of a magnet: the part which closes

the magnetic lines of the field-magnet, or the rotary part.

_Battery._—A combination of two or more voltaic cells

coupled together.

_B. A._—British Association.

_Block Station._—A central-station for the supply of

continuous buildings.

_Board of Trade Unit._—One thousand watt hours equals 10

ampères at 100 volts per hour, or 1·35 HP. working for one hour.

_Bobbin._—A coil of wire, or a number of such coils,

generally so mounted that they can be rapidly revolved.

_Bridge (Wheatstone’s)._—An apparatus for measuring

resistances by balancing the unknown resistance against one

known and capable of adjustment.

_B. W. G._—Birmingham wire gauge.

_Candle-Power._—Term used to denote the amount of

light as compared with a standard sperm candle, which is

a spermaceti candle, burning at the rate of 2 grains per

minute.

_Carbons._—The electrodes of arc lamps; the negative

plate of a battery.

_Carcel Lamp._—The French standard, equal to 9·4 candles.

_Capacity_ (K).—The powder of a surface to hold

electricity as “static charge.” A coulomb divided by a volt.

Its Unit is the Farad.

_Cathode._—The negative pole of a battery; the wire or

plate connected with the zinc or positive element of the

battery. The object on which a metallic deposit is to be

formed. (_v._ Anode).

_Centimetre._—The hundredth part of a metre.

_Cell._—Each separate vessel in which a chemical action

occurs, by which electricity is capable of being developed.

_Central-station._—A building containing plant for

supplying electricity to the public.

_C. G. S._—The centimetre-gramme-second system.

_Circuit Conductive._—The wires which form the path for

the passage of the current.

_Commutator._—A circuit changer, or switch. The collector

of currents on a dynamo.

_Compound Winding._—A method of increasing or decreasing

the energy developed in a dynamo in proportion to the demand.

_Conductivity._—Is the reciprocal to resistance, and

applies to that property of any substance whereby the

passage of electricity through it is effected with the least

opposition.

_Conductors._—Substances which most freely permit

electricity to pass.

_Connections._—Wires, &c., completing the circuit between

different apparatus.

_Contact Breaker._—The electric lighting equivalent for a

gas tap.

_Coulomb_ (Q).—The Unit of quantity, which passes in one

second of an ampère current.

_Cut-out._—An instrument placed in the circuit which will

open it automatically.

_Current_ (C).—The Unit is the Ampère. The supposed

flow or passage of electricity or electrical force in the

direction from + to -, or positive to negative.

_Current Reverse._—A current in the opposite direction to

the normal current.

_Decimetre._—The tenth part of a metre.

_Deflection._—The angle or number of degrees through

which the needle of a galvanometer moves when a current is

passing through its coils.

_Diaphragm._—A porous division between two liquids

through which electric current passes.

_Duplex Cut-out._—An instrument which enables a spare

fuse to be immediately substituted for that melted.

_Duty._—A term used to denote the economy of any motor.

_Dynamo._—A name given to machines which produce

electricity for commercial purposes.

_Dynamometer._—An instrument for ascertaining the

horse-power absorbed by any machine.

_Dyne._—The Unit of force which gives a velocity of 1

centimetre per second to 1 gramme weight after acting for 1

second.

_Direct-Current Dynamo._—An electric generator producing

currents passing in one direction.

_Earth._—A term for the return circuit, which for economy

is formed through the earth in telegraph work. A return

conductor common to many circuits is sometimes called

“earth.”

_Electrodes._—A term for the poles or plates leading the

current into and out of a cell.

_Electrolysis._—The act of decomposition by the electric

current.

_Electrolyte._—The liquid in a cell.

_Electrometer._—An instrument for measuring electric

potential.

_Electro-motive Force_ (_E. M. F._) (E).—The electric

force tending to produce electric current. The Unit is the

volt.

_Erg._—The C. G. S. Unit of energy. The work of moving a

body through 1 centimetre against the force of a dyne.

_Extra Current._—The induced current of higher E. M. F.,

which appears in a wire wound in a helix when the current is

broken.

_Farad._—The Unit of capacity: a coulomb divided by a

volt.

_Field of Force._—The space between or around the poles

of a magnet.

_Filament._—That part of an incandescent lamp which gives

out the light.

_Field-Magnets._—In a dynamo the magnets between which

the armature revolves.

_Foot Pound._—The British Unit of work, or 1 lb. raised 1

foot high.

_Galvanometer._—An instrument for measuring current.

_Generator._—Another term for a dynamo.

_Governor._—An apparatus for controlling the speed of any

motor.

_Horse-Power_ (_HP._)—indicated HP.—The Unit is 33,000

lbs. lifted 1 foot high per minute. The nominal HP. of

any motor is generally fixed considerably less than the

indicated.

2(A P R S)

Ind. HP. of any engine =  —————————

33,000

A = Area of piston in square inches.

P = Average pressure of steam in lbs. per square inch.

R = Number of revolutions per minute.

S = Length of stroke in feet (if in inches, × 33,000 by 12).

The French “force cheval” represents 32,560 foot pounds.

_Horse-Power of Water._—Indian Government rule, 15 cube

feet per second falling through 1 foot = 1 HP.

_Indicator Diagram._—The drawing produced by an

instrument which is fixed to the cylinder of a steam-engine

for the purpose of ascertaining its duty.

_Induction._—The name given to effects produced out of a

force-exerting body or out of the circuit to which the force

is directly applied. A current in a wire induces currents in

other conductors parallel to it.

_Inertia._—The resistance to change of state of rest or

motion.

_Insulators._—Bodies possessing high electrical

resistance. All insulating substances, however, allow some

electricity to pass.

_Intensity._—The old term for the properties now

described as E. M. F. and potential.

_Joule_, also called _Joulad_ (W).—The Unit of heat or

work, it has also been applied to the mechanical equivalent

of heat, 772 foot lbs.

_Kilowatt._—One thousand watts.

_Knot._—The geographical and nautical mile.

_Leads._—Terms usually applied to copper conductors.

_Magnetism._—A condition which can be highly developed in

iron and steel, by electric action or otherwise.

_Measurement._—See Units.

_Metre._—The French standard of length = 3·28 feet.

_Meg Ohm._—The prefix meg signifies a million.

_Millimetre._—The thousandth part of a metre.

_Milliampère._—The thousandth of an ampère.

_Mica-foil._—The fusible portion of a Hedges cut-out.

_Multiple Arc._—Galvanic cells or dynamos connected

parallel, or lamps so arranged that each furnishes a

separate path for the current.

_Negative._—In a machine the wire returning from the

lamp. In a galvanic battery the copper, carbon, or platinum

plate. Sign -.

_Nigger._—An American term used to denote an electrical

fault.

_Ohm._—The Unit of resistance. A volt divided by an

ampère.

_Ohm’s Laws._—Laws, investigated by Ohm, regulating

electrical current magnitudes. Calling the current C,

electro-motive force E, and resistance R: the expression is

Current            E. M. F.            Resistance.

E                                     E

C = ——, amps.    E = C × R, volts.    R = —— ohms.

R                                     C

(See Electrical Measurements.)

_Osmose._—The process of diffusion of liquids through a

porous division.

_Paraffin._—An insulating substance much used in

telegraphic work.

_Plummer Block._—The bearing on which a shaft revolves.

_Polarity._—The distinct features of the two separate

poles of a magnet.

_Poles._—The two ends of a magnet. The wires, plates,

&c., leading from a battery.

_Positive._—In a machine the wire proceeding to the lamp.

In a battery the zinc plate. Sign +.

_Potential._—A word used to indicate a condition for

work. Difference of potential is a difference of electrical

condition. Potential of a battery means its E. M. F.

_Power_ (P).—The rate of doing work. When an ampère

passes through an ohm, the unit power, called a watt, is

required.

_Quantity_ (Q).—The Unit is the Coulomb.

_Relay._—An electro-magnet which, receiving its current

from a distance, closes the circuit of a local battery so as

to produce the required effect of strength.

_Resistance_ (R).—The opposition presented by the circuit

to the development of the current. The Unit of resistance is

the Ohm.

_Rheostat._—An instrument for inserting resistances.

A valuable artificial resistance employed for measuring

unknown resistances.

_Return Current._—The current in the wire leading to the

machine.

_Rigger._—The pulley or wheel by which power is

transmitted.

_Secondary Battery._—Wrongly termed an accumulator, is an

appliance for storing energy in such a form that it shall be

available for the reproduction of electric currents.

_Secondary Generator._—A transformer of a current of high

potential into a current of less E. M. F.

_Series._—The plan of connecting lamps so that the

current passes one after the other.

_Shunt._—A coil of wire arranged to take a certain

proportion of any current.

_Solenoids._—Helices of wire which act like magnets.

_Switch._—An apparatus for changing one circuit on to

another.

_Spectrum._—The elongated figure of the prismatic colours.

_Torque._—Term used to express the strain on a shaft due

to electro-magnetic action.

_Units._—The various bases of any system of measurement.

_Volt._—The Unit of electro-motive force and potential.

An ampère multiplied by an ohm. (See Electrical

Measurements.)

_Voltameter._—An apparatus for measuring the current by

its chemical action.

_Voltmeter._—An instrument used for measuring E. M. F.

_Watt._—The Unit of power. A volt-ampère. The horse-power

electrical, taken as 746 B A watts, is equivalent to only

736 true watts. The horse-power electrical is equal to 756

B A watts, which is equal to 746 true watts. The “force de

cheval,” or horse-power in use abroad, is defined as 75

kilogrammetres, and is, therefore, 736 true watts.

_Work_ (W.)—Is a volt multiplied by a coulomb, or

(amp.² × sec × ohm) or (amp. × sec × volt). The Unit is the Joule.

_Yoke._—Is a term applied to the apparently neutral mass

of iron which connects the poles of a horse-shoe magnet at

the back.

[Illustration]

APPENDIX I.—PRINCIPAL ELECTRIC LIGHTING STATIONS IN GREAT BRITAIN.

-----------+--------------+-------------+-----------+-----------+

| Approximate  |             |Approximate|           |

|No. of Lights.|             | length of |           |

Name of   +--------+-----+   Systems   |  longest  |   Main    |

Station.  | Incan- |     |  employed.  |    main   | conductor |

| descent| Arc.|             |   supply  |overhead or|

| or Glow|     |             | conductor |underground|

|  Lamps.|     |             | in miles. |           |

-----------+--------+-----+-------------+-----------+-----------+

Brighton   |        |     |High-tension |           |           |

Electric-  |  1,800 |  40 |   lamps in  |    20     | Overhead  |

Light      |        |     |   multiple  |           |           |

Company    |        |     |series Brush |           |           |

|        |     |   Dynamos   |           |           |

-----------+--------+-----+-------------+-----------+-----------+

Cadogan    |        |     |             |           |           |

Electricity|        |     |   Edmunds’  |           |           |

Supply     |   · ·  | · · |    system   |     2     | Overhead  |

Company    |        |     | of Battery  |           |           |

(New       |        |     |Transformers |           |           |

Company)  |        |     |             |           |           |

-----------+--------+-----+-------------+-----------+-----------+

|        |     |Lowrie Hall  |           |  7 miles  |

Eastbourne |  1,700 |  30 |Transformers |    15     |  under-   |

|        |     |             |           |  ground   |

-----------+--------+-----+-------------+-----------+-----------+

|        |     |High-tension |           |           |

Grosvenor  |        |     |with Ferranti|     6     |           |

District   |        |     |Transformers | circuits, |           |

Electrical | 20,000 |  40 |   primary   |  total    |           |

Supply     |        |     | 2,400 volts,|  about    | Overhead  |

|        |     |  secondary  | 70 miles  |           |

|        |     |  200 volts, |           |           |

|        |     |  Ferranti   |           |           |

|        |     |   dynamos   |           |           |

-----------+--------+-----+-------------+-----------+-----------+

Kensington |        |     |   Crompton  |           |           |

Court      | 1600   |     |  105 volts  |           |           |

Electric   | to be  | · · | low-tension,|     ¼     |Underground|

Lighting   |extended|     |   constant  |           |           |

Company    |   to   |     |    supply   |           |           |

| 10,000 |     | by means of |           |           |

|        |     |accumulators |           |           |

-----------+--------+-----+-------------+-----------+-----------+

|        |     | Low-tension |           | Overhead  |

Liverpool  |  1,000 | · · | continuous  |   · ·     |    and    |

|        |     |  current    |           |Underground|

|        |     |  dynamos    |           |           |

-----------+--------+-----+-------------+-----------+-----------+

|        |     | Chamberlain |           |           |

Leamington |  1,500 | · · | and Hookham |           |Underground|

|        |     |dynamos with |    1¼     |           |

|        |     |accumulators |           |           |

-----------+--------+-----+-------------+-----------+-----------+

Paddington | 4,115  |  98 |  E. M. F.   |           |           |

Electric   |16 C. P.|3,000| 150 volts,  |           |           |

Lighting   |  lamps |C. P.|   Gordon    |     3     |Underground|

|        |     |alternating  |           |           |

|        |     |  current    |           |           |

|        |     |   Dynamos   |           |           |

-----------+--------+-----+-------------+-----------+-----------+

-----------+--------------+--------+--------+------------+

|              |        |        |            |

|              |        |        |  Charges.  |

Name of   | Approximate  |        |        |            |

Station.  |    area of   |Working |Hours of+------------+

| distribution.|Capital.|Supply. |            |

|              |        |        | By Meter.  |

-----------+--------------+--------+--------+------------+

Brighton   |              |        |        |  Meter     |

Electric-  |   About 3    |        |        |  rent,     |

Light      |   square     | £12,000|Constant|21_s._ 8_d._|

Company    |   miles      |        |        |    per     |

|              |        |        |   annum    |

-----------+--------------+--------+--------+------------+

Cadogan    |              |        |        |            |

Electricity|Belgravia and |        |        |            |

Supply     |   Cadogan    |        |        |            |

Company    |    Estate    | £20,000|   · ·  |    · ·     |

(New       |              |        |        |            |

Company)  |              |        |        |            |

-----------+--------------+--------+--------+------------+

|              |        |        |            |

Eastbourne |    · ·       | £20,000|Constant|     · ·    |

|              |        |        |            |

-----------+--------------+--------+--------+------------+

|Very irregular|        |        |            |

Grosvenor  |   district,  |        |        |  7½ per    |

District   |  a house is  |£375,000| 8 A.M. |  Board of  |

Electrical |   lighted    |        |   to   |   Trade    |

Supply     |   2 miles    |        | 3 A.M. |    unit    |

|   station    |        |        |            |

|   from the   |        |        |            |

|   station    |        |        |            |

|              |        |        |            |

-----------+--------------+--------+--------+------------+

| The streets  |        |        |            |

Kensington |   adjoining  |        |        |  By meter  |

Court      | the station, |        |        |and minimum |

Electric   | the mains to | £25,000|Constant| charge of  |

Lighting   | be continued |        |        | 10_s._ per |

Company    | to another   |        |        |  light per |

|  station at  |        |        |    annum   |

|Knightsbridge |        |        |            |

-----------+--------------+--------+--------+------------+

|              |        |        |            |

Liverpool  |              |        |        |  By meter  |

|     · ·      |£20,000 |  · ·   | on sliding |

|              |        |        |   scale    |

-----------+--------------+--------+--------+------------+

|              |        |        |            |

|              |        |        |            |

|              |        |        |            |

Leamington |      183     |        |        |            |

|     street   |   · ·  |Constant|            |

|     lamps    |        |        |    meter   |

|              |        |        |            |

-----------+--------------+--------+--------+------------+

Paddington |              |        |        |            |

Electric   |              |        |        |            |

Lighting   |   67 acres   |   · ·  |Constant|     · ·    |

|              |        |        |            |

-----------+--------------+--------+--------+------------+

-----------+---------------------------------+---------------------+

|                                 |                     |

|             Charges.            |                     |

Name of   |                                 |                     |

Station.  |---------------------------------+     Remarks.        |

|                                 |                     |

|     By yearly fixed amount.     |                     |

|                                 |                     |

-----------+---------------------------------+---------------------+

Brighton   | Glow lamps, 1_s._ per unit, or  | If consumption      |

Electric-  |  rather over ¾_d._ per lamp     |     is below        |

Light      | per hour. Arc lamps, 4_s_. per  |    100 units        |

Company    |      lamp per week including    |    quarterly,       |

|           maintenance           | 10¾_d._ discount.   |

-----------+---------------------------------+---------------------+

Cadogan    |                                 |                     |

Electricity|                                 |                     |

Supply     |                                 |                     |

Company    |             · ·                 |         · ·         |

(New       |                                 |                     |

Company)  |                                 |                     |

-----------+---------------------------------+---------------------+

|  According to consumption       |      A similar      |

Eastbourne |   averaging about 6½_d._        |       station       |

|             per unit            |     at Hastings.    |

-----------+---------------------------------+---------------------+

|                                 |                     |

Grosvenor  |                                 |                     |

District   |                                 |    A station at     |

Electrical |               · ·               |     Deptford is     |

Supply     |                                 |    under erection   |

|                                 |     to maintain     |

|                                 |   200,000 lights.   |

|                                 |                     |

|                                 |                     |

-----------+---------------------------------+---------------------+

|                                 |                     |

Kensington |8_d._ per unit, equal to 0·56_d._|                     |

Court      |  per 20 C.-P. lamp per hour,    |  District embraces  |

Electric   | or 0·28_d._ per 10 C.-P. lamp.  |  residences, shops, |

Lighting   |  Shops taken at £2 per annum    |  public hall, and   |

Company    |   per 20 C.-P. lamp minimum     |       church.       |

|         of 10 lights            |                     |

|                                 |                     |

-----------+---------------------------------+---------------------+

|                                 |   Board of Trade    |

Liverpool  | First 400 hours, 1_s._ per unit |  license for six    |

| Second  ”  ”     8_d._    ”     |years, hotels, shops,|

| Afterwards       4_d._    ”     |   and residences.   |

-----------+---------------------------------+---------------------+

|   Street lights £2 2_s._ per    |                     |

|      annum for 2,860 hours,     |                     |

|        including renewals.      |                     |

Leamington |1 to 40 units per quarter 8_d._  |                     |

| per unit. 41 to 150 units per   |          · ·        |

|  quarter, 6_d._ per unit. 151   |                     |

|units per quarter 4_d._ per unit |                     |

-----------+---------------------------------+---------------------+

Paddington |                                 |The district between |

Electric   |                                 |  Paddington and     |

Lighting   |    Worked by G. W. Railway      |  Westbourne Park is |

|                                 | lighted throughout. |

-----------+---------------------------------+---------------------+

--------------+-----------------+----------------+-----------+

|   Approximate   |                |Approximate|

|Number of Lights.|                | length of |

|-------+---------+                |  longest  |

Name of    | Incan-|         |System employed.|   main    |

Station.   |descent|   Arc.  |                |  supply   |

|or Glow|         |                | conductor |

| Lamps.|         |                |  in miles.|

--------------+-------+---------+----------------+-----------+

Barnet and    |       |         |                |           |

District      |       |         |                |     5     |

E. Supply     |  · ·  |   · ·   |  Joel Dynamos  |           |

Company       |       |         |                |           |

(New Company) |       |         |                |           |

--------------+-------+---------+----------------+-----------+

Chelsea       |       |         |                |           |

E. Supply     |  · ·  |   · ·   |      · ·       |    · ·    |

Company       |       |         |                |           |

(New Company) |       |         |                |           |

|       |         |                |           |

--------------+-------+---------+----------------+-----------+

St. James     |       |         |                |           |

and Pall      |  · ·  |   · ·   |   Continuous   |    · ·    |

Mall          |       |         |    current     |           |

(New Company) |       |         |                |           |

|       |         |                |           |

--------------+-------+---------+----------------+-----------+

|       |         |    Thompson    |           |

|       |         |    Houston     |    · ·    |

Taunton.      |  · ·  |   23    |   continuous   |           |

|       |         |    current     |           |

|       |         |                |           |

--------------+-------+---------+----------------+-----------+

Whitehall     |       |         |     Battery    |           |

Court         |  · ·  |   · ·   |   Transformer  |    · ·    |

(New Company) |       |         |     system     |           |

|       |         |                |           |

|       |         |                |           |

--------------+-------+---------+----------------+-----------+

Westminster   |  · ·  |   · ·   |      · ·       |    · ·    |

--------------+-------+---------+----------------+-----------+

West          |       |         |   Lowrie Hall  |  10 miles |

Brompton      |  · ·  |   · ·   |   Transformers |    when   |

|       |         |                | completed |

|       |         |                |           |

|       |         |                |           |

--------------+-------+---------+----------------+-----------+

Adelphi       |       |         |   Continuous   |     12    |

Theatre       | 4,000 |   · ·   |    current     |  external |

|       |         |    dynamos     |  circuits |

|       |         | coupled direct |           |

|       |         |   to engines   |           |

--------------+-------+---------+----------------+-----------+

Bath          |       |         |    Thomson     |           |

(New Company) |  · ·  |   85    |    Houston     |    · ·    |

|       |         |  Dynamos and   |           |

|       |         |  Transformers  |           |

--------------+-------+---------+----------------+-----------+

--------------+---------+-----------------+--------+--------+

|  Main   |                 |        |        |

|conductor|                 |        |        |

|overhead |Approximate area |Working |Hours of|

Name of    |or under-|of distribution. |Capital.| Supply.|

Station.   | ground. |                 |        |        |

--------------+---------+-----------------+--------+--------+

Barnet and    |Overhead |                 |        |        |

District      | chiefly |      · ·        | £5,000 |   · ·  |

E. Supply     |         |                 |        |        |

Company       |         |                 |        |        |

(New Company) |         |                 |        |        |

--------------+---------+-----------------+--------+--------+

Chelsea       |         |                 |        |        |

E. Supply     |   · ·   |      · ·        |   · ·  |   · ·  |

Company       |         |                 |        |        |

(New Company) |         |                 |        |        |

--------------+---------+-----------------+--------+--------+

St. James     |         |                 |        |        |

and Pall      |   · ·   |      · ·        | £20,000|   · ·  |

Mall          |         |                 |        |        |

(New Company) |         |                 |        |        |

--------------+---------+-----------------+--------+--------+

|         |                 |   · ·  |   · ·  |

Taunton.      |Overhead | Street lighting |        |        |

--------------+---------+-----------------+--------+--------+

Whitehall     |         |    To light     |        |        |

Court         |  · ·    |   hotels in     | £24,753|Constant|

(New Company) |         | Northumberland  |        |        |

|         |     Avenue      |        |        |

|         |                 |        |        |

--------------+---------+-----------------+--------+--------+

Westminster   |   · ·   |      · ·        |   · ·  |   · ·  |

--------------+---------+-----------------+--------+--------+

West          |         |                 |        |        |

Brompton      |   · ·   |      · ·        |   · ·  |Constant|

--------------+---------+-----------------+--------+--------+

Adelphi       |  Over-  |  The buildings  |        |        |

Theatre       |  head   |   are close     | Private|   · ·  |

|   and   |    together     |        |        |

| under-  |                 |        |        |

| ground  |                 |        |        |

--------------+---------+-----------------+--------+--------+

Bath          |         |                 |        |        |

(New Company) |   · ·   |   Arc lights    |   · ·  |   · ·  |

|         |   in streets    |        |        |

--------------+---------+-----------------+--------+--------+

-----------+----------------------------------+--------------------+

|             Charges.             |                    |

|                                  |                    |

Name of   +-----------+----------------------+                    |

Station.  | By Meter. |      By yearly       |       Remarks.     |

|           |    fixed amount.     |                    |

-----------+-----------+----------------------+--------------------+

Barnet and |           |                      |      71 lamps in   |

District   |    · ·    |         · ·          |   streets on posts |

E. Supply  |           |                      |     12 ft. high.   |

Company    |           |                      |                    |

(New        |           |                      |                    |

Company) |           |                      |                    |

-----------+-----------+----------------------+--------------------+

Chelsea    |           |                      |                    |

E. Supply  |    · ·    |         · ·          |         · ·        |

Company    |           |                      |                    |

(New       |           |                      |                    |

Company) |           |                      |                    |

-----------+-----------+----------------------+--------------------+

St. James  |           |                      |     Area to be     |

and Pall   |    · ·    |         · ·          |      lighted       |

Mall       |           |                      |     adjoining      |

(New       |           |                      |      station.      |

Company) |           |                      |                    |

-----------+-----------+----------------------+--------------------+

Taunton.   |    · ·    |  By yearly contract  |    Arc lamps of    |

|           |                      |     1200-C.-P.     |

-----------+-----------+----------------------+--------------------+

Whitehall  | Proposed  |  Proposed charge,    |     Amalgamated    |

Court      |  meter-   |  8_d._ per unit with |       with the     |

(New       |   rent    |   minimum of £1. 1   |   Metropolitan     |

Company) |10_s._ per |  per lamp per annum  |      Electric      |

| quarter   |                      |   Supply Company.  |

-----------+-----------+----------------------+--------------------+

Westminster|    · ·    |         · ·          |     New Company.   |

-----------+-----------+----------------------+--------------------+

West       |  By meter | The station is being erected by the House |

Brompton   |           |     to House Lighting Company, who also   |

|           | propose installations in other districts. |

-----------+-----------+-------------------------------------------+

Adelphi    |    · ·    |   The Adelphi Theatre, Adelaide Gallery,  |

Theatre    |           |      and Strand Restaurant are lit,       |

|           |   the machinery being fixed in a basement |

|           |    about 30 × 45 feet. No gas is laid on. |

-----------+-----------+----------------------+--------------------+

Bath       |           |                      | The power obtained |

(New       |    · ·    |   Yearly contract    |    from town weir  |

Company) |           |                      |     supplemented   |

|           |                      |   by steam-engine. |

-----------+-----------+----------------------+--------------------+

APPENDIX II.—PRINCIPAL ELECTRIC LIGHTING STATIONS ON THE CONTINENT.

--------------+---------------------+----------------+-----------+

|     Approximate     |                |Approximate|

|  Number of Lights.  |                | length of |

+-----------+---------+                |  longest  |

Name of    |   Incan-  |         |    System      |    main   |

Station.   |  descent  |   Arc.  |   employed.    |  supply   |

|  or Glow  |         |                | conductor |

|   Lamps.  |         |                | in miles. |

--------------+-----------+---------+----------------+-----------+

Bergen        |  3,000    |   70    |     Brush      |    · ·    |

--------------+-----------+---------+----------------+-----------+

Bellegarde    |    600    |   · ·   | Gramme dynamos |    · ·    |

--------------+-----------+---------+----------------+-----------+

Berlin        | 11,800    |   · ·   |  Edison lamps  |    · ·    |

|           |         |    100 volts   |           |

”           | 17,400    |   · ·   |       ”        |    1½     |

”           |  3,000    |   108   |       ”        |    · ·    |

”           | 42,200    |   400   |       ”        |    · ·    |

--------------+-----------+---------+----------------+-----------+

|           |         |                |           |

Breslau       |  5,000    |   69    |     Siemens    |    · ·    |

--------------+-----------+---------+----------------+-----------+

Brunswick     |  2,000    |   · ·   |      Edison    |    · ·    |

--------------+-----------+---------+----------------+-----------+

Crefeld       |  1,560    |   · ·   |        ”       |    · ·    |

--------------+-----------+---------+----------------+-----------+

Darmstadt     |  1,000    |   · ·   |        ”       |    · ·    |

--------------+-----------+---------+----------------+-----------+

Dresden       |  3,400    |   · ·   |        ”       |    · ·    |

--------------+-----------+---------+----------------+-----------+

Elberfeld     |  2,000    |   · ·   |        ”       |    · ·    |

--------------+-----------+---------+----------------+-----------+

Hamburg       |  4,000    |   50    |    Schuckert   |    · ·    |

--------------+-----------+---------+----------------+-----------+

Hernösand     |  · ·      |   70    |     Thomson    |    · ·    |

|           |         |     Houston    |           |

--------------+-----------+---------+----------------+-----------+

Halle         |  1,350    |   10    |      Edison    |    · ·    |

--------------+-----------+---------+----------------+-----------+

|  10,000   |         |                |           |

Hanover       |   to be   |         |                |           |

| increased |   · ·   |        ”       |    · ·    |

|    to     |         |                |           |

|  20,000   |         |                |           |

--------------+-----------+---------+----------------+-----------+

------------+---------+----------------+-----------------+--------+

|  Main   |                |                 |        |

|conductor|                |                 |        |

Name of  |overhead |Approximate area|  Description    |Hours of|

Station. |or under-|of distribution.|  of lighting.   | Supply.|

| ground. |                |                 |        |

------------+---------+----------------+-----------------+--------+

|         |                |    Street       |        |

Bergen      | Overhead|       · ·      |   lighting      |   · ·  |

|         |                |  and public     |        |

|         |                |   buildings     |        |

------------+---------+----------------+-----------------+--------+

Bellegarde  | Overhead|       · ·      |      · ·        |   · ·  |

------------+---------+----------------+-----------------+--------+

Berlin      |  Under- |  Nearly whole  | These instal-   |        |

|  ground |  of business   |    lations      |        |

|         |  part of city  |    supply       |Constant|

”         |    ”    |                |    clubs,       | service|

”         |    ”    |                |   theatres,     |        |

”         |    ”    |                |    public       |        |

|         |                |   buildings,    |        |

|         |                |     and         |        |

|         |                |street lighting  |        |

------------+---------+----------------+-----------------+--------+

|  Under- |  1,200 metres  |    Railway      |        |

Breslau     |  ground |     radius     |  station and    |   · ·  |

|         |                |     mills       |        |

------------+---------+----------------+-----------------+--------+

Brunswick   |    ”    |      · ·       |       · ·       |   · ·  |

------------+---------+----------------+-----------------+--------+

Crefeld     |    ”    |      · ·       |   Mills and     |   · ·  |

|         |                |   factories     |        |

------------+---------+----------------+-----------------+--------+

Darmstadt   |    ”    |      · ·       |       · ·       |   · ·  |

------------+---------+----------------+-----------------+--------+

Dresden     |    ”    |      · ·       |       · ·       |   · ·  |

------------+---------+----------------+-----------------+--------+

Elberfeld   |  Under- |   Three-wire   |       · ·       |   · ·  |

|  ground |     system     |                 |        |

------------+---------+----------------+-----------------+--------+

|         |                | Lighting of the |  Dusk  |

Hamburg     |    ”    |      · ·       |   Free Port     |  until |

|         |                |                 |  dawn  |

------------+---------+----------------+-----------------+--------+

Hernösand   | Overhead|      · ·       |       · ·       |   · ·  |

------------+---------+----------------+-----------------+--------+

Halle       |  Under- |      · ·       |  Stadt Theatre  |   · ·  |

|  ground |                |                 |        |

------------+---------+----------------+-----------------+--------+

Hanover     |    ”    |   13,000 feet  | Shops and public|Constant|

|         |     radius     |    buildings    |        |

|         |   from station |                 |        |

------------+---------+----------------+-----------------+--------+

--------------+------------------------------+--------------------+

|          Charges.            |                    |

+---------+--------------------+                    |

Name of    |By Meter.|     By yearly      |      Remarks.      |

Station.   |         |   fixed amount.    |                    |

--------------+---------+--------------------+--------------------+

Bergen        |   · ·   |       · ·          |        · ·         |

--------------+---------+--------------------+--------------------+

|         |    Of fr. 0·4 per  |                    |

|         |  hour, or 8 francs |     Worked by      |

Bellegarde    |   · ·   |    per month for   |    water power.    |

|         |      8-C.-P.       |                    |

--------------+---------+--------------------+--------------------+

Berlin        |         |6_s._ per year fixed|                    |

|         | charge, and ½_d._  | Stations at        |

|         |   per hour per     | Friedrich Street,  |

”           |   · ·   |  16-C.-P. lamp;    | Mauer Street,      |

”           |         |arc lamps, 6_d._ and| Schadou Street.    |

”           |         | 7_d._ per hour, and|                    |

|         |    60_s._ yearly   |                    |

|         |     per light      |                    |

--------------+---------+--------------------+--------------------+

Breslau       |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

Brunswick     |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

Crefeld       |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

Darmstadt     |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

Dresden       |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

Elberfeld     |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

|         |                    | Under construction.|

Hamburg       |   · ·   |        · ·         |  2 block stations, |

|         |                    |  1 central-station.|

--------------+---------+--------------------+--------------------+

|         |                    |Yearly contract,    |

Hernösand     |   · ·   |        · ·         | which is less than |

|         |                    | former lighting by |

|         |                    | oil.               |

--------------+---------+--------------------+--------------------+

Halle         |   · ·   |        · ·         |        · ·         |

--------------+---------+--------------------+--------------------+

|By meter |                    |                    |

Hanover       | to sub- |0·42_d._ per 10-    |                    |

| scribers| C.-P. lamp per     |        · ·         |

| for     | hour; 0·5_d._      |                    |

| three   | per 16-C.-P.       |                    |

| years   |                    |                    |

--------------+---------+--------------------+--------------------+

--------------+--------------------+--------------+-----------+

|    Approximate     |              |Approximate|

| Number of Lights.  |              | length of |

+--------------------+              |  longest  |

Name of    |  Incan-  |         |    System    |    main   |

Station.   | descent  |   Arc.  |   employed.  |  supply   |

| or Glow  |         |              | conductor |

|  Lamps.  |         |              | in miles. |

--------------+----------+---------+--------------+-----------+

|          |         |Zippernowsky  |           |

Lucerne       |      800 |   · ·   | high-tension |    4      |

|          |         | current with |           |

|          |         | transformers |           |

--------------+----------+---------+--------------+-----------+

Lubeck        |    2,000 |   · ·   |    Edison    |    · ·    |

--------------+----------+---------+--------------+-----------+

|   11,000 |    210  |    Edison    |     ¾     |

Milan         |          |         |              |           |

|    1,000 |   · ·   | Zippernowsky |     ”     |

--------------+----------+---------+--------------+-----------+

Munich        |    6,500 |    140  |    Edison    |     ”     |

--------------+----------+---------+--------------+-----------+

Rome          |   14,000 |   · ·   | Zippernowsky |     4     |

--------------+----------+---------+--------------+-----------+

Rotterdam     |    1,000 |   · ·   |    Edison    |    · ·    |

--------------+----------+---------+--------------+-----------+

|          |         |Edison, Three-|           |

St. Etienne   |    3,000 |   · ·   | wire system  |    · ·    |

--------------+----------+---------+--------------+-----------+

|          |         |  Edison and  |           |

Strassburg    |    1,800 |     62  |   Siemens    |    · ·    |

--------------+----------+---------+--------------+-----------+

Stuttgart     |    1,060 |   · ·   |      ”       |    · ·    |

--------------+----------+---------+--------------+-----------+

Schwerin      |    2,390 |   · ·   |      ”       |    · ·    |

--------------+----------+---------+--------------+-----------+

|          |         |Goulard high- |           |

Tivoli        |    1,000 |      6  |tension trans-|    18     |

|          |         |formers       |           |

--------------+----------+---------+--------------+-----------+

Tours         |    3,500 |   · ·   |    Goulard   |     3     |

--------------+----------+---------+--------------+-----------+

Terni         |    3,000 |   · ·   | Zippernowsky |    · ·    |

|          |         | Transformers |           |

--------------+----------+---------+--------------+-----------+

--------------+---------+----------------+---------------+--------+

|  Main   |                |  Description  |Hours of|

|conductor|  Approximate   |  of lighting. |Supply. |

|overhead |     area of    |               |        |

Name of    |or under-|  distribution  |               |        |

Station.   | ground. |                |               |        |

--------------+---------+----------------+---------------+--------+

|         |To be extended  |               | Dusk   |

Lucerne       |Overhead |  throughout    |  In hotels    |  until |

|         |   Lucerne      |               |  mid-  |

|         |                |               |  night |

--------------+---------+----------------+---------------+--------+

Lubeck        |    ”    |      · ·       |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

|         |                |               |        |

|  Under- |1½ square mile  |The district is|        |

Milan         |  ground |                | served in a   |Constant|

|         |Theatre with 460| similar manner|        |

|    ”    |lamps in houses | to gas        |        |

--------------+---------+----------------+---------------+--------+

Munich        |    ”    | Two theatres   |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

|         |     Hotels     |               | 4 P.M. |

Rome          |    ”    |      and       |      · ·      |   to   |

|         |     shops      |               | 1 A.M. |

--------------+---------+----------------+---------------+--------+

Rotterdam     |    ”    |      · ·       |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

St. Etienne   |    ”    |      · ·       |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

| Under-  |Railway station,| Also a block  |  Dusk  |

|  ground | and goods      |  station for  |  until |

Strassburg    |   and   | yards, 86 acres|  hotel and    |  day-  |

|  over-  | area           |  restaurants  |  light |

|  head   |                |               |        |

--------------+---------+----------------+---------------+--------+

Stuttgart     | Under-  |   Theatre      |      · ·      |   · ·  |

|  ground |                |               |        |

--------------+---------+----------------+---------------+--------+

Schwerin      |    ”    |      ”         |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

|         | Principally    |               |        |

Tivoli        | Overhead|   street       |      · ·      |   · ·  |

|         |   lighting     |               |        |

--------------+---------+----------------+---------------+--------+

Tours         |    ”    |      · ·       |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

Terni         |   · ·   | Town lighting  |      · ·      |   · ·  |

--------------+---------+----------------+---------------+--------+

--------------+-------------------------------+--------------------+

|          Charges.             |                    |

Name of    +---------+---------------------+                    |

Station.   |By Meter.|     By yearly       |      Remarks.      |

|         |   fixed amount.     |                    |

--------------+---------+---------------------+--------------------+

Lucerne       |   · ·   |        · ·          |Motive power, water.|

--------------+---------+---------------------+--------------------+

Lubeck        |   · ·   |        · ·          |         · ·        |

--------------+---------+---------------------+--------------------+

| Arc and |Installation charge  |                    |

| incan-  |    per lamp         |                    |

Milan         |descent  |per 10 candles, 8_s._|         · ·        |

|½_d._ per| ”  16   ”     28_s._|                    |

|ampère-  | ”  32   ”     56_s._|                    |

|hour     |   Arc lamp £2       |                    |

|         |  per annum rent     |                    |

--------------+---------+---------------------+--------------------+

Munich        |   · ·   |        · ·          |       · ·          |

--------------+---------+---------------------+--------------------+

|         |  Of 2·08_d._        |The installation is |

Rome          |   · ·   |   per 16 C.-P.      |  owned by the gas  |

|         |   lamp per hour     |      company.      |

--------------+---------+---------------------+--------------------+

Rotterdam     |   · ·   |        · ·          |         · ·        |

--------------+---------+---------------------+--------------------+

|         |3_s._ 5_d._ per 16   |                    |

St. Etienne   |  Meter  |C.-P. lamp per month,|         · ·        |

|         |also fixed sum of    |                    |

|         |2_s._ 11_d._ per lamp|                    |

--------------+---------+---------------------+--------------------+

|         |Net cost of lighting |                    |

|         |station, including   |                    |

|         | 12 per cent. for    |Carried out by the  |

|         |interest and renewal.|railway company. The|

Strassburg    |   · ·   |  —Arc lamps,        |cost is estimated at|

|         |3¾_d._ per hour;     |one-third less than |

|         |16 C.-P. glow lamps, |       gas.         |

|         |0·42_d._ per hour;   |                    |

|         |10 C.-P. glow lamps, |                    |

|         |0.32_d._ per hour; 8 |                    |

|         |C.-P. glow lamps,    |                    |

|         |0·29_d._ per hour    |                    |

--------------+---------+---------------------+--------------------+

Stuttgart     |   · ·   |        · ·          |One central-station.|

|         |                     | One block station. |

--------------+---------+---------------------+--------------------+

Schwerin      |   · ·   |        · ·          |         · ·        |

--------------+---------+---------------------+--------------------+

|         |                     |Motive power, water;|

Tivoli        |   · ·   |        · ·          | yearly contract for|

|         |                     | street lighting.   |

--------------+---------+---------------------+--------------------+

|         |Subscribers at 2_s._ |Three distributing  |

Tours         |   · ·   | 9_d._ per 16 C.-P.  | stations at work,  |

|         | lamp per month      | to be increased    |

|         |                     |      to ten.       |

--------------+---------+---------------------+--------------------+

Terni         |         |Charge 0·4_d._ to    |                    |

|   · ·   | 1·3_d._ per hour    |       · ·          |

|         | according to C.-P.  |                    |

--------------+---------+---------------------+--------------------+

--------------+---------------------+--------------+-----------+

|     Approximate     |              |Approximate|

|  Number of Lights.  |              | length of |

|---------------------+              |  longest  |

Name of    |   Incan-  |         |    System    |    main   |

Station.   |  descent  |   Arc.  |   employed.  |  supply   |

|  or Glow  |         |              | conductor |

|   Lamps.  |         |              | in miles. |

--------------+-----------+---------+--------------+-----------+

Treviso       |       800 |   · ·   | Zippernowsky |    · ·    |

|           |         | transformers |           |

--------------+-----------+---------+--------------+-----------+

Turin         |     1,000 |     100 |     Edison   |     · ·   |

--------------+-----------+---------+--------------+-----------+

|           |         |    Brush     |           |

Temesvar      |       760 |   · ·   |   machines;  |     2     |

|           |         |   Lane Fox   |           |

|           |         |    lamps     |           |

--------------+-----------+---------+--------------+-----------+

|           |         |Crompton Low- |           |

|           |         | tension      |           |

Vienna        |     8,000 |   · ·   | dynamos      |     ½     |

|           |         | with battery |           |

|           |         | transformers |           |

--------------+-----------+---------+--------------+-----------+

--------------+---------+-----------------+---------------+-------+

|  Main   |                 |               |       |

|conductor|   Approximate   |               |Hours  |

Name of    |overhead |     area of     |  Description  |  of   |

Station.   |or under-|   distribution  |  of lighting. |Supply.|

| ground. |                 |               |       |

--------------+---------+-----------------+---------------+-------+

Treviso       |Overhead |  Town lighting. |      · ·      |  · ·  |

--------------+---------+-----------------+---------------+-------+

Turin         | Under-  | Street lighting |      · ·      |  · ·  |

| ground  | by arc lamps    |               |       |

--------------+---------+-----------------+---------------+-------+

|         |  About 37 miles |     Street    | Dusk  |

Temesvar      |Overhead |  of streets     |    lighting   | until |

|         |                 |     chiefly   | dawn  |

--------------+---------+-----------------+---------------+-------+

|         | Opera house,    |               |       |

Vienna        | Under-  |  Court theatre, |      · ·      |  · ·  |

| ground  |  and municipal  |               |       |

|         |  buildings      |               |       |

--------------+---------+-----------------+---------------+-------+

--------------+----------------------------+---------------------+

|        Charges.            |                     |

+-------+--------------------+                     |

Name of    |  By   |     By yearly      |      Remarks.       |

Station.   | Meter.|   fixed amount.    |                     |

--------------+-------+--------------------+---------------------+

Treviso       |  · ·  |        · ·         |        · ·          |

|       |                    |                     |

--------------+-------+--------------------+---------------------+

Turin         |  · ·  |  Thomson-Houston   |        · ·          |

|       |     arc lamps      |                     |

--------------+-------+--------------------+---------------------+

|       |  Street lighting,  |                     |

|       |  1·5 kreutzer      |                     |

|       |   per 16-C.-P.     |                     |

Temesvar      |  · ·  |  lamp per hour     |        · ·          |

|       |                    |                     |

|       |Private consumers,  |                     |

|       |  1·81 kreutzer     |                     |

--------------+-------+--------------------+---------------------+

|       |                    |This installation is |

|       | By contract at a   | being put down by   |

Vienna        |  · ·  | price about double | the gas company     |

|       |      gas           | which lights the    |

|       |                    |     city.           |

--------------+-------+--------------------+---------------------+

INDEX.

Arc Lamps,

—— places where suitable, 10.

—— charges for, 10.

—— at Milan, 47.

Accumulators,

—— at Kensington Court, 69.

—— at Vienna, 76.

Birmingham wire gauge resistance table, 105.

—— in French measurements, 106.

Central-stations,

—— Siemens’ suggestion for, 1.

—— at Philadelphia, 2.

—— block, 3.

—— construction, 3.

—— selection of district for, 4.

—— relation between daily output and capacity, 7.

—— loss in, 15.

—— at Deptford, 31.

—— at Eastbourne, 31.

—— at Brighton, 32.

—— at Tours, 32.

—— at Vienna, 76.

—— position of, 16.

—— in United States, 17.

—— at Grosvenor Gallery, 27.

—— Kensington Court, 20, 68.

—— methods of lighting from, 20.

—— tables showing cost of, 86, 87.

Cost of gas compared with electricity, 8.

Cost of kerosene, 9.

Cost of arc lighting, 10.

Conductors,

—— relative size of, for different systems, 22.

—— arrangement of, at Grosvenor Gallery, 28.

—— primary conductors at Grosvenor Gallery, 30.

—— diagram of network system of, at Milan, 46.

—— diagram of multiple series system at Temesvar, 60.

—— conduits for, in New York, 92, 93, 94.

Distribution of Electricity,

—— Edison parallel system, 41.

—— Edison feeders, 42.

—— three-wire system, 43.

—— series system, 52.

—— Bernstein system, 57.

—— multiple series system, 58.

—— by means of secondary batteries, 65.

—— system of, at Kensington Court, 69.

Dynamotors, 79.

—— Swinburne’s Compound, 83.

Electric Lighting,

—— as an investment, 3, 9, 97.

—— people who most readily take it up, 4.

—— relation between number of lights used and number fixed, 4, 5.

—— cost of, to householder, 5.

—— diagram of, in London district, 6.

—— diagram of, at Cincinnati, 7.

—— charges for, 8.

—— description of arc and glow, 9.

—— at Tilbury Docks, 18.

—— at Victoria Station, 18.

—— at Paddington Station, 19.

—— relative cost of, for direct and transformer systems, 21, 27.

—— at Lucerne, 34.

—— at Milan, 34, 44.

—— cost of, at Milan, 48.

—— at Berlin, 52.

—— cost of, at Berlin, 53.

—— Bernstein system of, 55.

—— diagram of, system at Colchester, 67.

—— working cost of, at Athenæum Club, 88.

—— working cost of, at Naval and Military Club, 89.

—— working cost of, at South Kensington Museum, 89.

—— working cost of Thomson-Houston system of,

in an American city, 90.

Experiment at the Teatro dal Verone, 34.

Faults, discovery of, 51.

Gas Lights,

—— heat from, advantages and objections, 3.

—— number used and fixed, 4.

—— cost of, at Berlin, 53.

—— cost of, to householder, 5.

Glossary, 107.

Incandescent Lamps,

—— number obtained per electrical HP., 8.

—— illustration of, 11.

—— candle-power of, 11.

—— consumption of energy in, 10, 63.

—— life of, 11.

—— blackening of, 12.

—— at Temesvar, 63.

Lighting,

—— number of hours of, per annum, 4.

—— cost of, to London householder, 5.

—— diagram of, in London district, 6.

—— diagram of, at Cincinnati, 7.

—— diagram of, 13.

—— relative cost of, with direct and transformer system, 22.

—— relative cost of, by electricity and gas, 91.

Lucigen light, the, 99.

—— cost of working, 100.

Machinery at Grosvenor Gallery, 29.

Motors, Electric, 39.

—— diagram showing power supplied to, in Boston, 40.

—— purposes used for, in America, 39.

Meters, Electric,

—— the Edison, 49.

—— the Aron, 54.

Mackenzie’s conduits for electric light cables, 95.

Priestman’s petroleum engine, 98.

Regulation of E. M. F. at Grosvenor Gallery, 29.

Regulation of E. M. F. at Milan, 44.

Rent of meters at Milan, 49.

Rent of meters at Berlin, 53.

Regulators for secondary batteries, 76.

Resistance of Copper Wire, 105, 106.

Speed indicators at Grosvenor Gallery, 29.

Safety fuses at Grosvenor Gallery, 31.

Safety fuses at Milan, 47.

Switch, double pole, 72.

Table I. showing cost of laying conductors, 74, 75.

Table II. showing cost and maintenance of plant, 86, 87.

Table showing resistance, &c., of copper wire, 105, 106.

Table showing principal electric lighting stations

in Great Britain, 116-119.

Table showing principal electric lighting stations

on the Continent, 120-125.

Terms, explanation of, 107-115.

Transformers,

—— application of, 27.

—— diagram of Ruhmkorff type of, 23.

—— description of Ruhmkorff type of, 23.

—— arrangements of circuits of, 24.

—— two classes of, 24.

—— Kapp & Snell, 27.

—— distribution of electricity by means of, 21.

—— prevention of shocks from, 30.

—— Westinghouse converters, 35.

—— potential used in, 38.

—— direct current, 79.

—— comparison between alternate and direct current, 80.

—— Swinburne’s dynamotor, 83.

—— advantages of Zippernowsky-Deri system of, 34.

Turbines working the dynamos at Tivoli, 32.

Turbines working the dynamos at Lucerne, 33.

Useful Notes, 101-103.

—— incandescent lights, 102.

—— arc lighting of works, 102.

—— approximate cost, 102.

—— wire running, 103.

—— Electrical Measurements, 104.

Westinghouse system, 35.

—— at Pittsfield, 37.

Wires overhead or underground, 91.

[Illustration]

LONDON: PRINTED BY WILLIAM CLOWES AND SONS, LIMITED,

STAMFORD STREET AND CHARING CROSS.

THE

HOUSE-TO-HOUSE

Electric Light Supply Co., Ld.

(MODEL CENTRAL ELECTRIC LIGHTING STATION, KENSINGTON,

ADJOINING THE WEST BROMPTON STATION ON THE

METROPOLITAN DISTRICT RAILWAY)

_Are prepared to assist the formation

of_

LOCAL ELECTRIC LIGHT COMPANIES,

_and to erect_

CENTRAL-STATIONS

_for the distribution of Electricity in

any part of the Kingdom_.

Estimates for Complete Sets of Plant

furnished free of charge.

WILLIAM LOWRIE, _Engineer_.

H. St. JOHN WINKWORTH, _Secretary_,

117, Bishopsgate Street, London,

E.C.

_BY THE SAME AUTHOR._

PRECAUTIONS TO BE ADOPTED ON INTRODUCING

THE ELECTRIC LIGHT.

_INSURANCE RULES, &c._,

WITH

NOTES ON THE PREVENTION OF FIRE RISKS.

_Illustrated._ Price 2_s._ 0_d._

THE SUPPLY OF ELECTRICITY

BY LOCAL AUTHORITIES.

Demy 8vo. Illustrated. Price 1_s._

DISTRICT ELECTRICITY SUPPLY.

CENTRAL SUPPLY STATIONS WORKED ON

THE E.P.S.

AUTOMATIC SYSTEM FOR THE PUBLIC SUPPLY OF

ELECTRICITY FROM

STORAGE BATTERIES.

Descriptive Pamphlet Free.

EPITOME OF THE SYSTEM.

The generating plant is all placed in a

conveniently situated building within

or without the District to be Lighted.

Convenient Sub- or Storage-Stations

are selected throughout this District,

and contain sufficient Accumulators to

supply the maximum demand.

The Batteries in each of these

Storage-Stations are recharged

in series, _one-half at a time_,

throughout the System during the period

of minimum demand, and by the evening

are all full and ready to cope with the

heavy night work.

The whole of the charging, discharging,

and regulating apparatus is worked

automatically.

ADVANTAGES OF THE SYSTEM.

=_Reliability._=—The Light is

solely derived from Storage, and

is absolutely steady. There is no

connection whatever between the Lamp

and Moving Machinery.

The Supply is continuous day and night.

=_Economy in Prime Outlay._=—The

proportion of Engine Power in use to

the power required for maximum supply

is only about _one- third_, while any

system, if running direct, requires

a large portion of the plant to be

duplicated.

=_Economy in Working._=—The

generating station is only at work a

definite number of hours during the

daytime, after which period the plant

may be let out or utilized for other

purposes, such as motive power, &c.

=_Electro Motors_= for all

purposes can be driven from the

ordinary discharge mains. This is

impossible where alternating currents

are employed.

=GUARANTEE.=—The E.P.S. Co. undertake to supply

all the necessary renewals for the Storage

Batteries in use in the above system at the rate of

=12=% per annum on the actual first cost of

the Batteries.

E.P.S. Accumulators are already in use at the

following Central-Stations:—Vienna; Berlin;

Cadogan (London); Norwich; Taunton; Leamington;

St. Austell; Detroit, U.S.A.; Allentown, U.S.A.;

Blenheim, U.S.A.; Haverford, U.S.A.; Delaud, U.S.A.

_Districts Surveyed, Plans, Specifications

and Tenders submitted by the_

ELECTRICAL POWER STORAGE COMPANY, LTD.,

4 GREAT WINCHESTER STREET, LONDON, E.C.

TELEGRAMS, “STORAGE, LONDON.”      TELEPHONE NO. 338.

ANGLO-AMERICAN

Brush Electric Light Corporation, Ltd.

MANUFACTURERS OF

_BRUSH ARC DYNAMOS AND LAMPS._

Victoria Incandescence Dynamos and Lamps.

ALTERNATE CURRENT DYNAMO MACHINES.

Transformers. Motors.

_ALL FITTINGS FOR ARC AND INCANDESCENCE LIGHTING, Etc._

CONTRACTORS FOR

PRIVATE INSTALLATIONS OF ELECTRIC LIGHT.

CENTRAL ELECTRIC LIGHT STATIONS.

_INSTALLATIONS ON SHIPBOARD._

ELECTRICAL RAILWAYS AND TRAMWAYS.

Railway Train Lighting by Electricity.

INSTALLATIONS FOR TRANSMISSION OF

POWER, Etc. Etc.

The Corporation are prepared to undertake the

establishment of Central Electric Lighting Stations on the

high or low-tension continuous current systems, with or

without accumulators, or on the alternating current system

with transformers, as may be best suited to the requirements

of each particular case.

The Corporation invite enquiries from Municipalities,

Local Gas or Electrical Companies, or owners of Blocks of

Houses or Shops, for the erection of Central Generating

Stations, and the supply of Electricity, either on their own

account, or upon such terms and conditions as may be agreed

upon.

Full particulars on application to—

THE SECRETARY,

112, BELVEDERE ROAD, LONDON, S.E.

UNITED

ELECTRICAL ENGINEERING

COMPANY, LIMITED.

The company have exceptional facilities for carrying out

contracts at home or abroad in the various branches of

Electrical Engineering. They own several valuable patents in

connection with the =distribution of Electricity and its

application to industrial and domestic purposes=; they

are not, however, restricted to any special system, and give

particular attention to providing those appliances which are

best adapted to the purposes in view.

=The Works= are equipped for =manufacturing,

testing, and repairing, and form a valuable auxiliary to

extensive contract work=, enabling the Company to give

prompt attention to the demands of their clients.

Contractors for

CENTRAL ELECTRIC

SUPPLY STATIONS.

ELECTRIC LIGHT INSTALLATIONS.

TRANSMISSION OF POWER.

THE “TELPHER” SYSTEM

OF CHEAP TRANSPORT.

ELECTRIC TRAMS & RAILWAYS, &c.

_Please apply for complete list of

Electric Light and Power Supplies to_—

=36, ALBERT EMBANKMENT, LONDON, S.E.=

CARBON WORKS, BARNSLEY.

THE GLOBE ELECTRICAL AND

ENGINEERING COMPANY.

ELECTRICAL AND GENERAL ENGINEERS.

[Illustration]

_Contractors for Electric Lighting._

_And Manufacturers of Dynamos, Lamps, Switches,

Cut-outs, and every Appliance used in the

Installation of Electric Light._

NO. 1 DEPARTMENT comprises all Electric Light

Fittings, also Ornamental Electroliers, Pendants, Brackets,

Ceiling Plates, or Rosettes, Globe Lamps and Globe Lamp

Holders, also Glass Shades and Fringes in coloured glass of

many varieties.

NO. 2 DEPARTMENT. This includes the well known

brand of Globe Carbon Rods and Battery Plates, Galvanic

Batteries of all descriptions, Battery supplies or materials

such as terminals, zinc, crushed carbon, chemicals, jars,

and porous pots. Measuring Instruments, Galvanometers,

patent Speed Gauges, Ammeters and Voltmeters—the accuracy

of same certified and laboratory test supplied.

NO. 3 ELECTRICAL ENGINEERING. Dynamos,

Alternating and Continuous Current. Transformers,

Cable—plain, copper, lead coated; also of _the special

high insulation_ required by London Electrical Supply

Co.’s rules. Sundries for Central-Station Installation.

Special List will be sent on application. Telephones and

Transmitters. Sundries for Telephone Installations.

_Belting, Oils, Waste, Paint, Patent Jointing Mastic, &c., are kept

in Stock, also Cable, Silk and Cotton Covered Wire._

Address:—=The MANAGER=,

Offices—=7, CARTERET STREET=.

_Supply Stores: 20, Dartmouth Street, Westminster, S.W._

Telegraphic Address, “Globulous, London.”

CARBON WORKS, BARNSLEY.

THE

Globe Electrical & Engineering Company.

CARBON CUTTERS AND GRINDERS.

CARBON RODS.

[Illustration]

CARBON PLATES.

=ELECTRIC LIGHT CARBON RODS= (Fig. 6), cored and

solid, coppered and plain. All sizes in stock from 4 to 40⁽ᵐᵐ⁾.}

Makers of Sir James Douglas’s Rods (Fig. 4), as used by

the Trinity House.

=CARBON PLATES= for Leclanché Batteries, etc. (Fig. 3),

Consolidated Battery Plates, made to withstand nitric

acid or bichromate, can be supplied up to 13ins. + 10ins.

out of stock, and larger sizes to order.

=CARBON CELLS AND CYLINDERS= (Figs. 1, 2, and 5), of

all descriptions.

Experimental Carbon Goods of every description made to Order.

PRICES ON APPLICATION.

_Offices_:—=7, CARTERET ST., WESTMINSTER, S.W.=

THE GULCHER

ELECTRIC LIGHT & POWER CO., LTD.,

BATTERSEA FOUNDRY, BATTERSEA, LONDON, S.W.

Manufacturers of Electrical Machinery

OF EVERY DESCRIPTION.

Contractors to H.M. NAVY, H.M. WAR DEPARTMENT,

Sir W. G. ARMSTRONG & CO.,

OUDH AND ROHILKUND RAILWAY CO., etc., etc.

[Illustration]

THE COMPANY SUPPLY—

=DYNAMOS.= Series, Shunt, and Compound Wound.

=ARC LAMPS.= Projectors, Search Lights, etc.

=SWITCH BOARDS= and Fittings.

=ALTERNATING CURRENT DYNAMOS.=

=TRANSFORMERS.=

=SECONDARY BATTERIES.=

=COMPLETE INSTALLATIONS= for lighting =TOWNS=,

=PUBLIC BUILDINGS=, =MILLS=, =FACTORIES=,

=IRONWORKS=, and =COLLIERIES=, also =PRIVATE

HOUSES= and =MANSIONS=.

_SOLE CONTRACTORS for the PERMANENT LIGHTING of the CRYSTAL

PALACE, Sydenham, and the ROYAL AQUARIUM, WESTMINSTER,

also the CITY of WELLINGTON, New Zealand._

WOODHOUSE & RAWSON,

LIMITED.

Electrical Engineers and Contractors,

FOR THE

LIGHTING OF CITIES, TOWNS, FACTORIES, MILLS,

AND

PRIVATE RESIDENCES.

COMPLETE CENTRAL-STATION PLANT.

Houses Wired and Fitted throughout for connection

to Central-Station Circuits.

ESTIMATES ON APPLICATION. GOOD WORK AT MODERATE PRICES.

=11, QUEEN VICTORIA STREET, LONDON, E.C.=

_Contractors to the Chief Exhibitions, Stock Exchange,

Messrs. W. H. Smith & Sons, Peak, Frean & Co.,

Crosse & Blackwell, Grosvenor Gallery, &c., &c._

THE

Orient Electric Light Company

LIMITED.

[Illustration]

_Contractors for the supply of Electric Lighting Plant for

Private Houses, Public Buildings, Factories, Towns, &c.,

on the most approved system and at moderate cost._

QUOTATIONS GIVEN FOR TEMPORARY INSTALLATIONS.

Central-Stations Fitted Out, and Negotiations

carried on for same.

ESTIMATES AND QUOTATIONS FREE.

London Offices: 2, East India Avenue, E.C.

AGENTS ABROAD:

Messrs. GILLANDERS, ARBUTHNOT & CO.      Calcutta and Rangoon

Messrs. GORDON, WOODROFFE & CO.          Madras.

Messrs. EWART, LATHAM & CO.              Bombay.

_Crown 8vo., 128 pp., Limp cloth, 40 Illustrations. Price 2s. 6d._

PRECAUTIONS TO BE ADOPTED ON INTRODUCING

THE ELECTRIC LIGHT.

WITH NOTES ON THE PREVENTION OF FIRE RISKS.

CONTENTS.—_Fire Risk Committee—Resistance of

Conductors—Glow Lamps—Sizes of Main and Branch

Conductors—Standard and Birmingham Wire Gauge—Factors

for Calculation—Running of Wires—Switches—Connectors

and Joints—Insulators—Short Circuit—Cut-out, Fusible,

and Automatic—Lamp Holders—Life of Lamps, Electrical

Governor, Speed Gauge—Testing Insulation—Fires and

Accidents from Electric Current—Specification for

Electric Lighting—Instructions for Working—Phœnix

Fire Office Rules—American Fire Office Rules—Electrical

Measurements—Resistance of Copper and German

Silver—English and French Measure—Rules for Fusible

Mica-Foils—Rules for Direction of Current—Number of

Electric Lights to compare with Gas—Motive Power, Steam,

Gas—Motive Power, Water—Explanation of Terms—Price List._

OPINIONS OF THE PRESS.

_The Builder._

“Mr. Hedges points out clearly the risks that are

inseparable from slovenly work and incompetent handling,

and gives clear directions for carrying the main and branch

conductors and the lamp wires, and for calculating the sizes

of the various leads according to the number of lights to be

worked. He insists very properly that some regular system

should be followed, so that it should always be known which

is the positive and which the negative wire,—in other

words, which wire leads from the machine to the lamps, and

which is the return. In addition, however, to showing this

by mere position, _i.e._, by placing the positive wire on

the left side of the negative if vertical, and under it if

horizontal, we should strongly recommend that the insulating

covering should be of different colours on the two wires,

and thus any accidental displacement would not be of

consequence.”

_Revue Internationale de l’Electricité._

“Ce petit livre sans prétention contient une grande

quantité de renseignements pratiques. Tous ceux qui

s’occupent d’éclairage électrique trouveront grand profit à

le consulter.

“Dans les quatre-vingts pages que contient ce travail,

l’auteur a su rassembler toutes les indications nécessaires

et utiles pour effectuer les installations. Il n’était pas

possible de grouper d’une manière plus logique, plus claire

et plus concise les règles à suivre pour assurer le bon

fonctionnement d’une installation d’éclairage.

“L’auteur s’est étendu surtout sur la description et

l’installation des appareils de sùreté, sur la pose des

conducteurs et sur les diamètres à leur donner, sur l’essai

des circuits, etc....

“Un petit dictionnaire, donnent l’explication des terms

techniques, complète d’une manière heureuse ce petit guide

qui sera consulté avec autant de profit que bien d’autres

ouvrages plus étendus et conçus dans un esprit moins

pratique.

“AUG. M.”

_Copies of the above can be obtained from_

The Globe Electrical and Engineering Company,

7, CARTERET STREET, WESTMINSTER, S.W.

Manufacturers of Electrical Supplies.

E. AND F. N. SPON, LONDON.

_Crown 8vo. 156 pp. Cloth gilt. Price 3s._

Useful Information on Electric Lighting.

EMBODYING THE

RULES OF THE FIRE RISK COMMITTEE AND THE

ELECTRIC LIGHTING BILL;

ALSO

PLAIN DIRECTIONS FOR THE WORKING OF ELECTRIC LAMPS

AND DYNAMO MACHINES.

BY KILLINGWORTH HEDGES,

_M.I.C.E., M. Soc. Telegraph Engineers, F.C.S._

_CONTENTS.—Introductory Remarks—The Production of

Electricity—The Voltaic Arc—Division of the Electric

Light—Machines or Generators—Power required, and

Motors—Application of the Electric Light—Choice of a

System—Electrical Measurement—Cost of Working—Result

of Various Installations—Measurement of Light and

Current—Storage of Electricity and Transmission of

Power—Conclusion—Useful Tables and Memoranda._

_The Graphic_,

“At the present time, when the question of illumination

by electricity is fully under discussion, a third edition

of Mr. Killingworth Hedges’ _Useful Information on Electric

Lighting_ is doubly welcome. The little work is now fully

brought up to date, and gives a plain, straightforwardly

written account of the various forms of the arc and

incandescent lamps, and, indeed, of the general system of

electric lighting. Thus a very fair idea of the principle

may be gathered by the general reader, who will find it a

welcome companion when visiting the Electrical Exhibition,

while the manufacturer in search of a practicable light for

his workshop will gain valuable information from the various

hints conveyed in its pages. To the scientific student also

the work will be exceedingly useful, if only from the handy

memoranda and tables in the appendix. _Altogether the book

is the best of the kind that we have yet seen_, and we

cannot refrain from hoping that Mr. Killingworth Hedges may

see fit to bring out a more compendious and detailed work

on the subject, with which he is so eminently competent to

deal.”

_Also, by the same Author, demy 8vo.

Illustrated, 32 pp. Paper. Price 1s._

The Supply of Electricity by Local Authorities.

READ AT THE ANNUAL MEETING OF THE ASSOCIATION OF MUNICIPAL

ENGINEERS AND SURVEYORS, OXFORD, 1883.

All Mr. Hedges’ books are sent post free on receipt of

postal order, by the GLOBE ELECTRICAL AND ENGINEERING

COMPANY, Supply Stores, 7, Carteret Street, Westminster, S.W.

THE

BARNSLEY

CARBON COMPANY.

Wholesale Manufacturers of

PURE CARBON POINTS, CANDLES,

AND BATTERY PLATES OF EVERY DESCRIPTION.

CARBON CUTTERS AND GRINDERS.

CARBON WORKS:

=BARNSLEY,

YORKSHIRE=.

LONDON OFFICE:

7, Carteret Street,

Westminster, S.W.

J. EDMUNDSON & CO.,

LIMITED,

Engineers & Electricians,

19, GREAT GEORGE ST., WESTMINSTER, S.W.

Electric Lighting for Country

and Town Mansions, &c.

=J. EDMUNDSON & CO.=, invite an inspection of their

Complete System of Lighting COUNTRY and TOWN

MANSIONS, by means of Incandescent Electric Lights.

=A COMPLETE INSTALLATION= consisting of =DYNAMO

MACHINE=, =ENGINE=, =STORAGE BATTERY and

LAMPS=, may be seen working at J. E. & Co.’s =SHOW

ROOMS, 19, GREAT GEORGE STREET, WESTMINSTER=, where

all information, including Estimates of Cost, &c., may be

obtained.

ESTIMATES ALSO GIVEN FOR TEMPORARY LIGHTING BY MEANS OF

STORAGE BATTERIES, FOR BALLS, RECEPTIONS, &c.

SPECIAL AGENTS FOR

EDISON & SWAN LAMPS.

Special Terms to the Trade.

MANUFACTURERS OF ELECTROLIERS, BRACKETS,

AND

All Descriptions of Electric Light Fittings.

Central-Station Lighting.

[Illustration]

_THE KAPP TRANSFORMER._

THE CONNAUGHT

alternating current Dynamo.

(KAPP’S PATENT.)

SHARP AND KENT,

ENGINEERS AND ELECTRICIANS,

_Connaught Mansions, Victoria St., Westminster, S.W._

TELEGRAPHIC ADDRESS—

“=MEGAVOLT, LONDON.=”          =TELEPHONE, 3,125=

DR. ARONS ELECTRICITY METERS

For Alternate and Continuous Current. Used in all the most

Important Central-Stations in the World.

[Illustration]

THE GENERAL ELECTRIC CO.,

(G. BINSWANGER & CO.) _Manufacturers and Suppliers of_

The APOSTLE Carbons. | China and Glass Ware,

Switches, Lamps, Cables, Casings, &c.

_The best without exception._| _In great variety_.

Electrical Fittings of every description.

=LONDON=:

THE GENERAL ELECTRIC CO.,

5, GREAT ST. THOMAS APOSTLE,

LONDON, E.C.

_Telegrams: “Electricity.”_

_Telephone: “1887.”_

=MANCHESTER=:

MANCHESTER ELECTRIC WORKS CO.,

(G. BINSWANGER, _Managing Director_),

45, CHAPEL STREET, SALFORD,

MANCHESTER.

_Telegrams: “Induction.”_

THE GLOBE ELECTRICAL AND

ENGINEERING COMPANY.

_Offices_:—=7, CARTERET ST., WESTMINSTER, S.W.=

MANUFACTURERS OF

HEDGES’ PATENT SAFETY CATCHES, OR CUT-OUTS,

WITH

FUSIBLE SAFETY PLUGS AND OF ALBO METAL MICA-FOILS.

[Illustration]

DIRECTIONS FOR INSERTING A SPARE MICA-FOIL.—Undo

the Contact Screws, lift the Contact Pieces and place Foil

fairly under, and screw down, taking care not to jam the

Mica on to the Foil, which should be loose, so as to allow

for expansion.

_Certificate from the Vienna Exhibition,

which was protected throughout by

“Hedges’ Patent Fuses.”_

[TRANSLATION.]

THE PATENT HEDGES’ CUT-OUTS have found a useful sphere

of employment in the labours of the Technical Scientific

Commission, and their construction has proved itself most

admirably adapted to the ends in view.

The President of the Technical Scientific Commission,

VIENNA, _13th May, 1884_.

(_Signed_) F. STEFAN.

W. T. GOOLDEN & CO.,

Electrical Engineers,

_Contractors to Her Majesty’s Government

and the Principal Railway Companies._

Sole Manufacturers of the Connaught (Kapp’s Patent)

Alternating Current Dynamo and Transformers;

GOOLDEN-RAVENSHAW CONTINUOUS CURRENT DYNAMO;

Electric Motors for all purposes;

MEASURING INSTRUMENTS;

CARDEW VOLTMETERS

(The only Reliable Instruments for Alternating Currents);

Evershed Patent Gravity Voltmeters and Ammeters

(Not affected by the proximity of dynamos).

Complete Estimates furnished for Central-Stations, Plant for

Alternating and Direct Currents, or for Batteries, Engines,

Boilers, etc., by the Best Makers only, and of the most

economical types.

ALL PLANTS SUPPLIED CAN BE TESTED AT OUR OWN WORKS.

_Offices and Works_:

WOODFIELD ROAD, WESTBOURNE PARK, LONDON, W.

End of the Project Gutenberg EBook of Central-Station Electric Lighting, by

Killingworth Hedges

*** END OF THIS PROJECT GUTENBERG EBOOK CENTRAL-STATION ELECTRIC LIGHTING ***

***** This file should be named 61219-0.txt or 61219-0.zip *****

This and all associated files of various formats will be found in:

http://www.gutenberg.org/6/1/2/1/61219/

Produced by Chris Curnow, Paul Marshall and the Online

Distributed Proofreading Team at http://www.pgdp.net (This

file was produced from images generously made available

by The Internet Archive)

Updated editions will replace the previous one--the old editions will

be renamed.

Creating the works from print editions not protected by U.S. copyright

law means that no one owns a United States copyright in these works,

so the Foundation (and you!) can copy and distribute it in the United

States without permission and without paying copyright

royalties. Special rules, set forth in the General Terms of Use part

of this license, apply to copying and distributing Project

Gutenberg-tm electronic works to protect the PROJECT GUTENBERG-tm

concept and trademark. Project Gutenberg is a registered trademark,

and may not be used if you charge for the eBooks, unless you receive

specific permission. If you do not charge anything for copies of this

eBook, complying with the rules is very easy. You may use this eBook

for nearly any purpose such as creation of derivative works, reports,

performances and research. They may be modified and printed and given

away--you may do practically ANYTHING in the United States with eBooks

not protected by U.S. copyright law. Redistribution is subject to the

trademark license, especially commercial redistribution.

START: FULL LICENSE

THE FULL PROJECT GUTENBERG LICENSE

PLEASE READ THIS BEFORE YOU DISTRIBUTE OR USE THIS WORK

To protect the Project Gutenberg-tm mission of promoting the free

distribution of electronic works, by using or distributing this work

(or any other work associated in any way with the phrase "Project

Gutenberg"), you agree to comply with all the terms of the Full

Project Gutenberg-tm License available with this file or online at

www.gutenberg.org/license.

Section 1. General Terms of Use and Redistributing Project

Gutenberg-tm electronic works

1.A. By reading or using any part of this Project Gutenberg-tm

electronic work, you indicate that you have read, understand, agree to

and accept all the terms of this license and intellectual property

(trademark/copyright) agreement. If you do not agree to abide by all

the terms of this agreement, you must cease using and return or

destroy all copies of Project Gutenberg-tm electronic works in your

possession. If you paid a fee for obtaining a copy of or access to a

Project Gutenberg-tm electronic work and you do not agree to be bound

by the terms of this agreement, you may obtain a refund from the

person or entity to whom you paid the fee as set forth in paragraph

1.E.8.

1.B. "Project Gutenberg" is a registered trademark. It may only be

used on or associated in any way with an electronic work by people who

agree to be bound by the terms of this agreement. There are a few

things that you can do with most Project Gutenberg-tm electronic works

even without complying with the full terms of this agreement. See

paragraph 1.C below. There are a lot of things you can do with Project

Gutenberg-tm electronic works if you follow the terms of this

agreement and help preserve free future access to Project Gutenberg-tm

electronic works. See paragraph 1.E below.

1.C. The Project Gutenberg Literary Archive Foundation ("the

Foundation" or PGLAF), owns a compilation copyright in the collection

of Project Gutenberg-tm electronic works. Nearly all the individual

works in the collection are in the public domain in the United

States. If an individual work is unprotected by copyright law in the

United States and you are located in the United States, we do not

claim a right to prevent you from copying, distributing, performing,

displaying or creating derivative works based on the work as long as

all references to Project Gutenberg are removed. Of course, we hope

that you will support the Project Gutenberg-tm mission of promoting

free access to electronic works by freely sharing Project Gutenberg-tm

works in compliance with the terms of this agreement for keeping the

Project Gutenberg-tm name associated with the work. You can easily

comply with the terms of this agreement by keeping this work in the

same format with its attached full Project Gutenberg-tm License when

you share it without charge with others.

1.D. The copyright laws of the place where you are located also govern

what you can do with this work. Copyright laws in most countries are

in a constant state of change. If you are outside the United States,

check the laws of your country in addition to the terms of this

agreement before downloading, copying, displaying, performing,

distributing or creating derivative works based on this work or any

other Project Gutenberg-tm work. The Foundation makes no

representations concerning the copyright status of any work in any

country outside the United States.

1.E. Unless you have removed all references to Project Gutenberg:

1.E.1. The following sentence, with active links to, or other

immediate access to, the full Project Gutenberg-tm License must appear

prominently whenever any copy of a Project Gutenberg-tm work (any work

on which the phrase "Project Gutenberg" appears, or with which the

phrase "Project Gutenberg" is associated) is accessed, displayed,

performed, viewed, copied or distributed:

This eBook is for the use of anyone anywhere in the United States and

most other parts of the world at no cost and with almost no

restrictions whatsoever. You may copy it, give it away or re-use it

under the terms of the Project Gutenberg License included with this

eBook or online at www.gutenberg.org. If you are not located in the

United States, you'll have to check the laws of the country where you

are located before using this ebook.

1.E.2. If an individual Project Gutenberg-tm electronic work is

derived from texts not protected by U.S. copyright law (does not

contain a notice indicating that it is posted with permission of the

copyright holder), the work can be copied and distributed to anyone in

the United States without paying any fees or charges. If you are

redistributing or providing access to a work with the phrase "Project

Gutenberg" associated with or appearing on the work, you must comply

either with the requirements of paragraphs 1.E.1 through 1.E.7 or

obtain permission for the use of the work and the Project Gutenberg-tm

trademark as set forth in paragraphs 1.E.8 or 1.E.9.

1.E.3. If an individual Project Gutenberg-tm electronic work is posted

with the permission of the copyright holder, your use and distribution

must comply with both paragraphs 1.E.1 through 1.E.7 and any

additional terms imposed by the copyright holder. Additional terms

will be linked to the Project Gutenberg-tm License for all works

posted with the permission of the copyright holder found at the

beginning of this work.

1.E.4. Do not unlink or detach or remove the full Project Gutenberg-tm

License terms from this work, or any files containing a part of this

work or any other work associated with Project Gutenberg-tm.

1.E.5. Do not copy, display, perform, distribute or redistribute this

electronic work, or any part of this electronic work, without

prominently displaying the sentence set forth in paragraph 1.E.1 with

active links or immediate access to the full terms of the Project

Gutenberg-tm License.

1.E.6. You may convert to and distribute this work in any binary,

compressed, marked up, nonproprietary or proprietary form, including

any word processing or hypertext form. However, if you provide access

to or distribute copies of a Project Gutenberg-tm work in a format

other than "Plain Vanilla ASCII" or other format used in the official

version posted on the official Project Gutenberg-tm web site

(www.gutenberg.org), you must, at no additional cost, fee or expense

to the user, provide a copy, a means of exporting a copy, or a means

of obtaining a copy upon request, of the work in its original "Plain

Vanilla ASCII" or other form. Any alternate format must include the

full Project Gutenberg-tm License as specified in paragraph 1.E.1.

1.E.7. Do not charge a fee for access to, viewing, displaying,

performing, copying or distributing any Project Gutenberg-tm works

unless you comply with paragraph 1.E.8 or 1.E.9.

1.E.8. You may charge a reasonable fee for copies of or providing

access to or distributing Project Gutenberg-tm electronic works

provided that

* You pay a royalty fee of 20% of the gross profits you derive from

the use of Project Gutenberg-tm works calculated using the method

you already use to calculate your applicable taxes. The fee is owed

to the owner of the Project Gutenberg-tm trademark, but he has

agreed to donate royalties under this paragraph to the Project

Gutenberg Literary Archive Foundation. Royalty payments must be paid

within 60 days following each date on which you prepare (or are

legally required to prepare) your periodic tax returns. Royalty

payments should be clearly marked as such and sent to the Project

Gutenberg Literary Archive Foundation at the address specified in

Section 4, "Information about donations to the Project Gutenberg

Literary Archive Foundation."

* You provide a full refund of any money paid by a user who notifies

you in writing (or by e-mail) within 30 days of receipt that s/he

does not agree to the terms of the full Project Gutenberg-tm

License. You must require such a user to return or destroy all

copies of the works possessed in a physical medium and discontinue

all use of and all access to other copies of Project Gutenberg-tm

works.

* You provide, in accordance with paragraph 1.F.3, a full refund of

any money paid for a work or a replacement copy, if a defect in the

electronic work is discovered and reported to you within 90 days of

receipt of the work.

* You comply with all other terms of this agreement for free

distribution of Project Gutenberg-tm works.

1.E.9. If you wish to charge a fee or distribute a Project

Gutenberg-tm electronic work or group of works on different terms than

are set forth in this agreement, you must obtain permission in writing

from both the Project Gutenberg Literary Archive Foundation and The

Project Gutenberg Trademark LLC, the owner of the Project Gutenberg-tm

trademark. Contact the Foundation as set forth in Section 3 below.

1.F.

1.F.1. Project Gutenberg volunteers and employees expend considerable

effort to identify, do copyright research on, transcribe and proofread

works not protected by U.S. copyright law in creating the Project

Gutenberg-tm collection. Despite these efforts, Project Gutenberg-tm

electronic works, and the medium on which they may be stored, may

contain "Defects," such as, but not limited to, incomplete, inaccurate

or corrupt data, transcription errors, a copyright or other

intellectual property infringement, a defective or damaged disk or

other medium, a computer virus, or computer codes that damage or

cannot be read by your equipment.

1.F.2. LIMITED WARRANTY, DISCLAIMER OF DAMAGES - Except for the "Right

of Replacement or Refund" described in paragraph 1.F.3, the Project

Gutenberg Literary Archive Foundation, the owner of the Project

Gutenberg-tm trademark, and any other party distributing a Project

Gutenberg-tm electronic work under this agreement, disclaim all

liability to you for damages, costs and expenses, including legal

fees. YOU AGREE THAT YOU HAVE NO REMEDIES FOR NEGLIGENCE, STRICT

LIABILITY, BREACH OF WARRANTY OR BREACH OF CONTRACT EXCEPT THOSE

PROVIDED IN PARAGRAPH 1.F.3. YOU AGREE THAT THE FOUNDATION, THE

TRADEMARK OWNER, AND ANY DISTRIBUTOR UNDER THIS AGREEMENT WILL NOT BE

LIABLE TO YOU FOR ACTUAL, DIRECT, INDIRECT, CONSEQUENTIAL, PUNITIVE OR

INCIDENTAL DAMAGES EVEN IF YOU GIVE NOTICE OF THE POSSIBILITY OF SUCH

DAMAGE.

1.F.3. LIMITED RIGHT OF REPLACEMENT OR REFUND - If you discover a

defect in this electronic work within 90 days of receiving it, you can

receive a refund of the money (if any) you paid for it by sending a

written explanation to the person you received the work from. If you

received the work on a physical medium, you must return the medium

with your written explanation. The person or entity that provided you

with the defective work may elect to provide a replacement copy in

lieu of a refund. If you received the work electronically, the person

or entity providing it to you may choose to give you a second

opportunity to receive the work electronically in lieu of a refund. If

the second copy is also defective, you may demand a refund in writing

without further opportunities to fix the problem.

1.F.4. Except for the limited right of replacement or refund set forth

in paragraph 1.F.3, this work is provided to you 'AS-IS', WITH NO

OTHER WARRANTIES OF ANY KIND, EXPRESS OR IMPLIED, INCLUDING BUT NOT

LIMITED TO WARRANTIES OF MERCHANTABILITY OR FITNESS FOR ANY PURPOSE.

1.F.5. Some states do not allow disclaimers of certain implied

warranties or the exclusion or limitation of certain types of

damages. If any disclaimer or limitation set forth in this agreement

violates the law of the state applicable to this agreement, the

agreement shall be interpreted to make the maximum disclaimer or

limitation permitted by the applicable state law. The invalidity or

unenforceability of any provision of this agreement shall not void the

remaining provisions.

1.F.6. INDEMNITY - You agree to indemnify and hold the Foundation, the

trademark owner, any agent or employee of the Foundation, anyone

providing copies of Project Gutenberg-tm electronic works in

accordance with this agreement, and any volunteers associated with the

production, promotion and distribution of Project Gutenberg-tm

electronic works, harmless from all liability, costs and expenses,

including legal fees, that arise directly or indirectly from any of

the following which you do or cause to occur: (a) distribution of this

or any Project Gutenberg-tm work, (b) alteration, modification, or

additions or deletions to any Project Gutenberg-tm work, and (c) any

Defect you cause.

Section 2. Information about the Mission of Project Gutenberg-tm

Project Gutenberg-tm is synonymous with the free distribution of

electronic works in formats readable by the widest variety of

computers including obsolete, old, middle-aged and new computers. It

exists because of the efforts of hundreds of volunteers and donations

from people in all walks of life.

Volunteers and financial support to provide volunteers with the

assistance they need are critical to reaching Project Gutenberg-tm's

goals and ensuring that the Project Gutenberg-tm collection will

remain freely available for generations to come. In 2001, the Project

Gutenberg Literary Archive Foundation was created to provide a secure

and permanent future for Project Gutenberg-tm and future

generations. To learn more about the Project Gutenberg Literary

Archive Foundation and how your efforts and donations can help, see

Sections 3 and 4 and the Foundation information page at

www.gutenberg.org Section 3. Information about the Project Gutenberg

Literary Archive Foundation

The Project Gutenberg Literary Archive Foundation is a non profit

501(c)(3) educational corporation organized under the laws of the

state of Mississippi and granted tax exempt status by the Internal

Revenue Service. The Foundation's EIN or federal tax identification

number is 64-6221541. Contributions to the Project Gutenberg Literary

Archive Foundation are tax deductible to the full extent permitted by

U.S. federal laws and your state's laws.

The Foundation's principal office is in Fairbanks, Alaska, with the

mailing address: PO Box 750175, Fairbanks, AK 99775, but its

volunteers and employees are scattered throughout numerous

locations. Its business office is located at 809 North 1500 West, Salt

Lake City, UT 84116, (801) 596-1887. Email contact links and up to

date contact information can be found at the Foundation's web site and

official page at www.gutenberg.org/contact

For additional contact information:

Dr. Gregory B. Newby

Chief Executive and Director

gbnewby@pglaf.org

Section 4. Information about Donations to the Project Gutenberg

Literary Archive Foundation

Project Gutenberg-tm depends upon and cannot survive without wide

spread public support and donations to carry out its mission of

increasing the number of public domain and licensed works that can be

freely distributed in machine readable form accessible by the widest

array of equipment including outdated equipment. Many small donations

($1 to $5,000) are particularly important to maintaining tax exempt

status with the IRS.

The Foundation is committed to complying with the laws regulating

charities and charitable donations in all 50 states of the United

States. Compliance requirements are not uniform and it takes a

considerable effort, much paperwork and many fees to meet and keep up

with these requirements. We do not solicit donations in locations

where we have not received written confirmation of compliance. To SEND

DONATIONS or determine the status of compliance for any particular

state visit www.gutenberg.org/donate

While we cannot and do not solicit contributions from states where we

have not met the solicitation requirements, we know of no prohibition

against accepting unsolicited donations from donors in such states who

approach us with offers to donate.

International donations are gratefully accepted, but we cannot make

any statements concerning tax treatment of donations received from

outside the United States. U.S. laws alone swamp our small staff.

Please check the Project Gutenberg Web pages for current donation

methods and addresses. Donations are accepted in a number of other

ways including checks, online payments and credit card donations. To

donate, please visit: www.gutenberg.org/donate

Section 5. General Information About Project Gutenberg-tm electronic works.

Professor Michael S. Hart was the originator of the Project

Gutenberg-tm concept of a library of electronic works that could be

freely shared with anyone. For forty years, he produced and

distributed Project Gutenberg-tm eBooks with only a loose network of

volunteer support.

Project Gutenberg-tm eBooks are often created from several printed

editions, all of which are confirmed as not protected by copyright in

the U.S. unless a copyright notice is included. Thus, we do not

necessarily keep eBooks in compliance with any particular paper

edition.

Most people start at our Web site which has the main PG search

facility: www.gutenberg.org

This Web site includes information about Project Gutenberg-tm,

including how to make donations to the Project Gutenberg Literary

Archive Foundation, how to help produce our new eBooks, and how to

subscribe to our email newsletter to hear about new eBooks.